## F1_(6-7)
[7 empty] | CASE A | [6 empty] | ENS
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 916.6313
0.025 | 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | B | 6354.6875
0.025 |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | C | 1108.5687
0.025 |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | D | 2038.6875
0.025 |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | E | 916.6313
0.025 |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | F | 6354.6875
0.025 |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
0.025 |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0 | 0
0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1062 | 4.7838 | 0.415 | 0.45909 | 2.3125 | 11.0625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1025 | 4.7676 | 0.415 | 0.45754 | 2.3125 | 11.025
[10 empty] | Total | 0.91663 | 4.625 | 22.0875
| 20 | total customers
| 175200 | total (customers*8760)
| 4.625 | total F
| 0.23125 | SAIFI=total F/total customers
| 1.1044 | SAIDI=total G/total customers
| 4.7757 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012607 | ASUI=1-ASAI
| 916.6313 | ENS=total ENS*1000
| 45.8316 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.415 | 3.1773 | 9.1875 | 76.5625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.415 | 3.1773 | 9.1875 | 76.5625
[10 empty] | Total | 6.3547 | 18.375 | 153.125
| 20 | total customers
| 175200 | total (customers*8760)
| 18.375 | total F
| 0.91875 | SAIFI=total F/total customers
| 7.6562 | SAIDI=total G/total customers
| 8.3333 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.000874 | ASUI=1-ASAI
| 6354.6875 | ENS=total ENS*1000
| 317.7344 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.3375 | 5.7838 | 0.415 | 0.55506 | 2.3125 | 13.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.3337 | 5.7676 | 0.415 | 0.55351 | 2.3125 | 13.3375
[10 empty] | Total | 1.1086 | 4.625 | 26.7125
| 20 | total customers
| 175200 | total (customers*8760)
| 4.625 | total F
| 0.23125 | SAIFI=total F/total customers
| 1.3356 | SAIDI=total G/total customers
| 5.7757 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015247 | ASUI=1-ASAI
| 1108.5687 | ENS=total ENS*1000
| 55.4284 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 2.4562 | 2.6735 | 0.415 | 1.0193 | 9.1875 | 24.5625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 2.4562 | 2.6735 | 0.415 | 1.0193 | 9.1875 | 24.5625
[10 empty] | Total | 2.0387 | 18.375 | 49.125
| 20 | total customers
| 175200 | total (customers*8760)
| 18.375 | total F
| 0.91875 | SAIFI=total F/total customers
| 2.4562 | SAIDI=total G/total customers
| 2.6735 | CAIDI=SAIDI/SAIFI
| 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00028039 | ASUI=1-ASAI
| 2038.6875 | ENS=total ENS*1000
| 101.9344 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1062 | 4.7838 | 0.415 | 0.45909 | 2.3125 | 11.0625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1025 | 4.7676 | 0.415 | 0.45754 | 2.3125 | 11.025
[10 empty] | Total | 0.91663 | 4.625 | 22.0875
| 20 | total customers
| 175200 | total (customers*8760)
| 4.625 | total F
| 0.23125 | SAIFI=total F/total customers
| 1.1044 | SAIDI=total G/total customers
| 4.7757 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012607 | ASUI=1-ASAI
| 916.6313 | ENS=total ENS*1000
| 45.8316 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.415 | 3.1773 | 9.1875 | 76.5625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.415 | 3.1773 | 9.1875 | 76.5625
[10 empty] | Total | 6.3547 | 18.375 | 153.125
| 20 | total customers
| 175200 | total (customers*8760)
| 18.375 | total F
| 0.91875 | SAIFI=total F/total customers
| 7.6562 | SAIDI=total G/total customers
| 8.3333 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.000874 | ASUI=1-ASAI
| 6354.6875 | ENS=total ENS*1000
| 317.7344 | AENS=ENS/total customers

## F3_(16-17)
[7 empty] | CASE A | [6 empty] | ENS
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 908.85
0.025 | 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | B | 6342.2375
0.025 |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | C | 1135.025
0.025 |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | D | 2026.2375
0.025 |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | E | 908.85
0.025 |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | F | 6342.2375
0.025 |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
0.025 |  |  | 30 | 0.6 | 0.025 | 0.015 | 0 | 0
0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.1006 | 4.9466 | 0.415 | 0.45676 | 2.225 | 11.0062
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.0894 | 4.8961 | 0.415 | 0.45209 | 2.225 | 10.8938
[10 empty] | Total | 0.90885 | 4.45 | 21.9
| 20 | total customers
| 175200 | total (customers*8760)
| 4.45 | total F
| 0.2225 | SAIFI=total F/total customers
| 1.095 | SAIDI=total G/total customers
| 4.9213 | CAIDI=SAIDI/SAIFI
| 0.99988 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.000125 | ASUI=1-ASAI
| 908.85 | ENS=total ENS*1000
| 45.4425 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.415 | 3.1711 | 9.1375 | 76.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.415 | 3.1711 | 9.1375 | 76.4125
[10 empty] | Total | 6.3422 | 18.275 | 152.825
| 20 | total customers
| 175200 | total (customers*8760)
| 18.275 | total F
| 0.91375 | SAIFI=total F/total customers
| 7.6413 | SAIDI=total G/total customers
| 8.3625 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00087229 | ASUI=1-ASAI
| 6342.2375 | ENS=total ENS*1000
| 317.1119 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.3675 | 6.1461 | 0.415 | 0.56751 | 2.225 | 13.675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.3675 | 6.1461 | 0.415 | 0.56751 | 2.225 | 13.675
[10 empty] | Total | 1.135 | 4.45 | 27.35
| 20 | total customers
| 175200 | total (customers*8760)
| 4.45 | total F
| 0.2225 | SAIFI=total F/total customers
| 1.3675 | SAIDI=total G/total customers
| 6.1461 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015611 | ASUI=1-ASAI
| 1135.025 | ENS=total ENS*1000
| 56.7512 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 2.4412 | 2.6717 | 0.415 | 1.0131 | 9.1375 | 24.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 2.4412 | 2.6717 | 0.415 | 1.0131 | 9.1375 | 24.4125
[10 empty] | Total | 2.0262 | 18.275 | 48.825
| 20 | total customers
| 175200 | total (customers*8760)
| 18.275 | total F
| 0.91375 | SAIFI=total F/total customers
| 2.4412 | SAIDI=total G/total customers
| 2.6717 | CAIDI=SAIDI/SAIFI
| 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00027868 | ASUI=1-ASAI
| 2026.2375 | ENS=total ENS*1000
| 101.3119 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.1006 | 4.9466 | 0.415 | 0.45676 | 2.225 | 11.0062
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.0894 | 4.8961 | 0.415 | 0.45209 | 2.225 | 10.8938
[10 empty] | Total | 0.90885 | 4.45 | 21.9
| 20 | total customers
| 175200 | total (customers*8760)
| 4.45 | total F
| 0.2225 | SAIFI=total F/total customers
| 1.095 | SAIDI=total G/total customers
| 4.9213 | CAIDI=SAIDI/SAIFI
| 0.99988 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.000125 | ASUI=1-ASAI
| 908.85 | ENS=total ENS*1000
| 45.4425 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.415 | 3.1711 | 9.1375 | 76.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.415 | 3.1711 | 9.1375 | 76.4125
[10 empty] | Total | 6.3422 | 18.275 | 152.825
| 20 | total customers
| 175200 | total (customers*8760)
| 18.275 | total F
| 0.91375 | SAIFI=total F/total customers
| 7.6413 | SAIDI=total G/total customers
| 8.3625 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00087229 | ASUI=1-ASAI
| 6342.2375 | ENS=total ENS*1000
| 317.1119 | AENS=ENS/total customers

## F4_(24-25)
[7 empty] | CASE A | [6 empty] | ENS
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 911.4438
0.025 | 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | B | 7222.0375
0.025 |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | C | 1108.5687
0.025 |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | D | 2076.0375
0.025 |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | E | 911.4438
0.025 |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | F | 7222.0375
0.025 |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
0.025 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
0.025 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.415 | 0.45806 | 2.1375 | 11.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.415 | 0.45339 | 2.1 | 10.925
[10 empty] | Total | 0.91144 | 4.2375 | 21.9625
| 20 | total customers
| 175200 | total (customers*8760)
| 4.2375 | total F
| 0.21188 | SAIFI=total F/total customers
| 1.0981 | SAIDI=total G/total customers
| 5.1829 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012536 | ASUI=1-ASAI
| 911.4438 | ENS=total ENS*1000
| 45.5722 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.415 | 3.611 | 10.3375 | 87.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.415 | 3.611 | 10.3375 | 87.0125
[10 empty] | Total | 7.222 | 20.675 | 174.025
| 20 | total customers
| 175200 | total (customers*8760)
| 20.675 | total F
| 1.0337 | SAIFI=total F/total customers
| 8.7012 | SAIDI=total G/total customers
| 8.4172 | CAIDI=SAIDI/SAIFI
| 0.99901 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00099329 | ASUI=1-ASAI
| 7222.0375 | ENS=total ENS*1000
| 361.1019 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.415 | 0.55662 | 2.1375 | 13.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.415 | 0.55195 | 2.1 | 13.3
[10 empty] | Total | 1.1086 | 4.2375 | 26.7125
| 20 | total customers
| 175200 | total (customers*8760)
| 4.2375 | total F
| 0.21188 | SAIFI=total F/total customers
| 1.3356 | SAIDI=total G/total customers
| 6.3038 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015247 | ASUI=1-ASAI
| 1108.5687 | ENS=total ENS*1000
| 55.4284 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.415 | 1.038 | 10.3375 | 25.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.415 | 1.038 | 10.3375 | 25.0125
[10 empty] | Total | 2.076 | 20.675 | 50.025
| 20 | total customers
| 175200 | total (customers*8760)
| 20.675 | total F
| 1.0337 | SAIFI=total F/total customers
| 2.5012 | SAIDI=total G/total customers
| 2.4196 | CAIDI=SAIDI/SAIFI
| 0.99971 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00028553 | ASUI=1-ASAI
| 2076.0375 | ENS=total ENS*1000
| 103.8019 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.415 | 0.45806 | 2.1375 | 11.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.415 | 0.45339 | 2.1 | 10.925
[10 empty] | Total | 0.91144 | 4.2375 | 21.9625
| 20 | total customers
| 175200 | total (customers*8760)
| 4.2375 | total F
| 0.21188 | SAIFI=total F/total customers
| 1.0981 | SAIDI=total G/total customers
| 5.1829 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012536 | ASUI=1-ASAI
| 911.4438 | ENS=total ENS*1000
| 45.5722 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.415 | 3.611 | 10.3375 | 87.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.415 | 3.611 | 10.3375 | 87.0125
[10 empty] | Total | 7.222 | 20.675 | 174.025
| 20 | total customers
| 175200 | total (customers*8760)
| 20.675 | total F
| 1.0337 | SAIFI=total F/total customers
| 8.7012 | SAIDI=total G/total customers
| 8.4172 | CAIDI=SAIDI/SAIFI
| 0.99901 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00099329 | ASUI=1-ASAI
| 7222.0375 | ENS=total ENS*1000
| 361.1019 | AENS=ENS/total customers

## F7_(38)
[7 empty] | CASE A | [6 empty] | ENS
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 452.35
0.025 | 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | B | 3172.675
0.025 |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | C | 570.625
0.025 |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | D | 1014.675
0.025 |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | E | 452.35
0.025 |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | F | 3172.675
0.025 |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 66 | 0.8 | 0.025 | 0.02 | 0 | 0
0.025 |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.09 | 4.8444 | 0.415 | 0.45235 | 2.25 | 10.9
[10 empty] | Total | 0.45235 | 2.25 | 10.9
| 10 | total customers
| 87600 | total (customers*8760)
| 2.25 | total F
| 0.225 | SAIFI=total F/total customers
| 1.09 | SAIDI=total G/total customers
| 4.8444 | CAIDI=SAIDI/SAIFI
| 0.99988 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012443 | ASUI=1-ASAI
| 452.35 | ENS=total ENS*1000
| 45.235 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.415 | 3.1727 | 9.15 | 76.45
[10 empty] | Total | 3.1727 | 9.15 | 76.45
| 10 | total customers
| 87600 | total (customers*8760)
| 9.15 | total F
| 0.915 | SAIFI=total F/total customers
| 7.645 | SAIDI=total G/total customers
| 8.3552 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00087272 | ASUI=1-ASAI
| 3172.675 | ENS=total ENS*1000
| 317.2675 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.375 | 6.1111 | 0.415 | 0.57062 | 2.25 | 13.75
[10 empty] | Total | 0.57062 | 2.25 | 13.75
| 10 | total customers
| 87600 | total (customers*8760)
| 2.25 | total F
| 0.225 | SAIFI=total F/total customers
| 1.375 | SAIDI=total G/total customers
| 6.1111 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015696 | ASUI=1-ASAI
| 570.625 | ENS=total ENS*1000
| 57.0625 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 2.445 | 2.6721 | 0.415 | 1.0147 | 9.15 | 24.45
[10 empty] | Total | 1.0147 | 9.15 | 24.45
| 10 | total customers
| 87600 | total (customers*8760)
| 9.15 | total F
| 0.915 | SAIFI=total F/total customers
| 2.445 | SAIDI=total G/total customers
| 2.6721 | CAIDI=SAIDI/SAIFI
| 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00027911 | ASUI=1-ASAI
| 1014.675 | ENS=total ENS*1000
| 101.4675 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.09 | 4.8444 | 0.415 | 0.45235 | 2.25 | 10.9
[10 empty] | Total | 0.45235 | 2.25 | 10.9
| 10 | total customers
| 87600 | total (customers*8760)
| 2.25 | total F
| 0.225 | SAIFI=total F/total customers
| 1.09 | SAIDI=total G/total customers
| 4.8444 | CAIDI=SAIDI/SAIFI
| 0.99988 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012443 | ASUI=1-ASAI
| 452.35 | ENS=total ENS*1000
| 45.235 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.415 | 3.1727 | 9.15 | 76.45
[10 empty] | Total | 3.1727 | 9.15 | 76.45
| 10 | total customers
| 87600 | total (customers*8760)
| 9.15 | total F
| 0.915 | SAIFI=total F/total customers
| 7.645 | SAIDI=total G/total customers
| 8.3552 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00087272 | ASUI=1-ASAI
| 3172.675 | ENS=total ENS*1000
| 317.2675 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 916.6313 | 20 | 6354.6875 | 20 | 1108.5687 | 20 | 2038.6875 | 20 | 916.6313 | 20 | 6354.6875 | 20
Feeder 3 | 908.85 | 20 | 6342.2375 | 20 | 1135.025 | 20 | 2026.2375 | 20 | 908.85 | 20 | 6342.2375 | 20
Feeder 4 | 911.4438 | 20 | 7222.0375 | 20 | 1108.5687 | 20 | 2076.0375 | 20 | 911.4438 | 20 | 7222.0375 | 20
Feeder 7 | 452.35 | 10 | 3172.675 | 10 | 570.625 | 10 | 1014.675 | 10 | 452.35 | 10 | 3172.675 | 10
TOTAL | 3189.275 | 70 | 23091.6375 | 70 | 3922.7875 | 70 | 7155.6375 | 70 | 3189.275 | 70 | 23091.6375 | 70
Analytic | 3.1893 |  | 23.0916 |  | 3.9228 |  | 7.1556 |  | 3.1893 |  | 23.0916
Monte Carlo_Code | 3.1882 |  | 23.091 |  | 3.8565 |  | 7.1517 |  | 3.1871 |  | 23.088
Deviation | 0.033707 |  | 0.0027607 |  | 1.6898 |  | 0.055027 |  | 0.068197 |  | 0.015752
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 3.1894 | 3.1873 | 3.1904 | 3.1882 |  | 945000 | 23.089 | 23.097 | 23.1 | 23.091
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 3.8544 | 3.8561 | 3.8565 | 3.8564 |  | 47500 | 7.165 | 7.1453 | 7.1657 | 7.1517
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 3.178 | 3.1805 | 3.1912 | 3.1871 |  | 1140000 | 23.088 | 23.023 | 23.095 | 23.099