## F1_(1-5)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2944.4813
0.1 | 0.025 | 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | B | 20518.75
0.1 | 0.025 |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | C | 3564.2313
0.1 | 0.025 |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | D | 4937.5312
0.1 | 0.025 |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | E | 2944.4813
0.1 | 0.025 |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | F | 10023.6719
0.1 | 0.025 |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
0.1 | 0.025 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | Calculation |  |  | 0.2075 |  | 1.0913 | 5.259 | 0.545 | 0.59473 | 45.65 | 240.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21125 |  | 1.1025 | 5.2189 | 0.545 | 0.60086 | 46.475 | 242.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.0913 | 5.259 | 0.545 | 0.59473 | 45.65 | 240.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.23125 |  | 1.1062 | 4.7838 | 0.545 | 0.60291 | 50.875 | 243.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.23125 |  | 1.1025 | 4.7676 | 0.5 | 0.55125 | 46.25 | 220.5
[11 empty] | Total | 2.9445 | 234.9 | 1186.575
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 234.9 | total F
|  | 0.2175 | SAIFI=total F/total customers
|  | 1.0987 | SAIDI=total G/total customers
|  | 5.0514 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00012542 | ASUI=1-ASAI
|  | 2944.4813 | ENS=total ENS*1000
|  | 2.7264 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.545 | 4.1727 | 202.125 | 1684.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.545 | 4.1727 | 202.125 | 1684.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.545 | 4.1727 | 202.125 | 1684.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.545 | 4.1727 | 202.125 | 1684.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.5 | 3.8281 | 183.75 | 1531.25
[11 empty] | Total | 20.5188 | 992.25 | 8268.75
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 992.25 | total F
|  | 0.91875 | SAIFI=total F/total customers
|  | 7.6562 | SAIDI=total G/total customers
|  | 8.3333 | CAIDI=SAIDI/SAIFI
|  | 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.000874 | ASUI=1-ASAI
|  | 20518.75 | ENS=total ENS*1000
|  | 18.9988 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.3225 | 6.3735 | 0.545 | 0.72076 | 45.65 | 290.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21125 |  | 1.3337 | 6.3136 | 0.545 | 0.72689 | 46.475 | 293.425
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.3225 | 6.3735 | 0.545 | 0.72076 | 45.65 | 290.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.23125 |  | 1.3375 | 5.7838 | 0.545 | 0.72894 | 50.875 | 294.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.23125 |  | 1.3337 | 5.7676 | 0.5 | 0.66687 | 46.25 | 266.75
[11 empty] | Total | 3.5642 | 234.9 | 1436.325
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 234.9 | total F
|  | 0.2175 | SAIFI=total F/total customers
|  | 1.3299 | SAIDI=total G/total customers
|  | 6.1146 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015182 | ASUI=1-ASAI
|  | 3564.2313 | ENS=total ENS*1000
|  | 3.3002 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 1.4469 | 1.5748 | 0.545 | 0.78855 | 202.125 | 318.3125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 1.4563 | 1.585 | 0.545 | 0.79366 | 202.125 | 320.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 1.4469 | 1.5748 | 0.545 | 0.78855 | 202.125 | 318.3125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 2.4562 | 2.6735 | 0.545 | 1.3387 | 202.125 | 540.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 2.4562 | 2.6735 | 0.5 | 1.2281 | 183.75 | 491.25
[11 empty] | Total | 4.9375 | 992.25 | 1988.625
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 992.25 | total F
|  | 0.91875 | SAIFI=total F/total customers
|  | 1.8413 | SAIDI=total G/total customers
|  | 2.0042 | CAIDI=SAIDI/SAIFI
|  | 0.99979 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0002102 | ASUI=1-ASAI
|  | 4937.5312 | ENS=total ENS*1000
|  | 4.5718 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.0913 | 5.259 | 0.545 | 0.59473 | 45.65 | 240.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21125 |  | 1.1025 | 5.2189 | 0.545 | 0.60086 | 46.475 | 242.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.0913 | 5.259 | 0.545 | 0.59473 | 45.65 | 240.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.23125 |  | 1.1062 | 4.7838 | 0.545 | 0.60291 | 50.875 | 243.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.23125 |  | 1.1025 | 4.7676 | 0.5 | 0.55125 | 46.25 | 220.5
[11 empty] | Total | 2.9445 | 234.9 | 1186.575
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 234.9 | total F
|  | 0.2175 | SAIFI=total F/total customers
|  | 1.0987 | SAIDI=total G/total customers
|  | 5.0514 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00012542 | ASUI=1-ASAI
|  | 2944.4813 | ENS=total ENS*1000
|  | 2.7264 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 1.4938 | 1.6259 | 0.545 | 0.81409 | 202.125 | 328.625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 2.5406 | 2.7653 | 0.545 | 1.3846 | 202.125 | 558.9375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 3.5781 | 3.8946 | 0.545 | 1.9501 | 202.125 | 787.1875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 5.6219 | 6.119 | 0.545 | 3.0639 | 202.125 | 1236.8125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91875 |  | 5.6219 | 6.119 | 0.5 | 2.8109 | 183.75 | 1124.375
[11 empty] | Total | 10.0237 | 992.25 | 4035.9375
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 992.25 | total F
|  | 0.91875 | SAIFI=total F/total customers
|  | 3.737 | SAIDI=total G/total customers
|  | 4.0675 | CAIDI=SAIDI/SAIFI
|  | 0.99957 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0004266 | ASUI=1-ASAI
|  | 10023.6719 | ENS=total ENS*1000
|  | 9.2812 | AENS=ENS/total customers

## F3_(11-15)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2896.5656
0.1 | 0.025 | 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | B | 20134.6937
0.1 | 0.025 |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | C | 3531.8312
0.1 | 0.025 |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | D | 4864.2719
0.1 | 0.025 |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | E | 2896.5656
0.1 | 0.025 |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | F | 10740.7719
0.1 | 0.025 |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
0.1 | 0.025 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | Calculation |  |  | 0.20875 |  | 1.1044 | 5.2904 | 0.545 | 0.60188 | 45.925 | 242.9625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.1006 | 5.3042 | 0.545 | 0.59984 | 45.65 | 242.1375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.1006 | 5.3042 | 0.545 | 0.59984 | 45.65 | 242.1375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2225 |  | 1.0894 | 4.8961 | 0.5 | 0.54469 | 44.5 | 217.875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2225 |  | 1.1006 | 4.9466 | 0.5 | 0.55031 | 44.5 | 220.125
[11 empty] | Total | 2.8966 | 226.225 | 1165.2375
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 226.225 | total F
|  | 0.21342 | SAIFI=total F/total customers
|  | 1.0993 | SAIDI=total G/total customers
|  | 5.1508 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00012549 | ASUI=1-ASAI
|  | 2896.5656 | ENS=total ENS*1000
|  | 2.7326 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.545 | 4.1645 | 201.025 | 1681.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.545 | 4.1645 | 201.025 | 1681.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.545 | 4.1645 | 201.025 | 1681.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.5 | 3.8206 | 182.75 | 1528.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.5 | 3.8206 | 182.75 | 1528.25
[11 empty] | Total | 20.1347 | 968.575 | 8099.725
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 968.575 | total F
|  | 0.91375 | SAIFI=total F/total customers
|  | 7.6413 | SAIDI=total G/total customers
|  | 8.3625 | CAIDI=SAIDI/SAIFI
|  | 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00087229 | ASUI=1-ASAI
|  | 20134.6937 | ENS=total ENS*1000
|  | 18.995 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.20875 |  | 1.3262 | 6.3533 | 0.545 | 0.72281 | 45.925 | 291.775
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.3225 | 6.3735 | 0.545 | 0.72076 | 45.65 | 290.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.3225 | 6.3735 | 0.545 | 0.72076 | 45.65 | 290.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2225 |  | 1.3675 | 6.1461 | 0.5 | 0.68375 | 44.5 | 273.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2225 |  | 1.3675 | 6.1461 | 0.5 | 0.68375 | 44.5 | 273.5
[11 empty] | Total | 3.5318 | 226.225 | 1420.675
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 226.225 | total F
|  | 0.21342 | SAIFI=total F/total customers
|  | 1.3403 | SAIDI=total G/total customers
|  | 6.2799 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.000153 | ASUI=1-ASAI
|  | 3531.8312 | ENS=total ENS*1000
|  | 3.3319 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 1.4569 | 1.5944 | 0.545 | 0.794 | 201.025 | 320.5125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 1.4538 | 1.591 | 0.545 | 0.79229 | 201.025 | 319.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 2.4412 | 2.6717 | 0.545 | 1.3305 | 201.025 | 537.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 2.4412 | 2.6717 | 0.5 | 1.2206 | 182.75 | 488.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 1.4538 | 1.591 | 0.5 | 0.72688 | 182.75 | 290.75
[11 empty] | Total | 4.8643 | 968.575 | 1956.4125
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 968.575 | total F
|  | 0.91375 | SAIFI=total F/total customers
|  | 1.8457 | SAIDI=total G/total customers
|  | 2.0199 | CAIDI=SAIDI/SAIFI
|  | 0.99979 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00021069 | ASUI=1-ASAI
|  | 4864.2719 | ENS=total ENS*1000
|  | 4.5889 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.20875 |  | 1.1044 | 5.2904 | 0.545 | 0.60188 | 45.925 | 242.9625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.1006 | 5.3042 | 0.545 | 0.59984 | 45.65 | 242.1375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2075 |  | 1.1006 | 5.3042 | 0.545 | 0.59984 | 45.65 | 242.1375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2225 |  | 1.0894 | 4.8961 | 0.5 | 0.54469 | 44.5 | 217.875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.2225 |  | 1.1006 | 4.9466 | 0.5 | 0.55031 | 44.5 | 220.125
[11 empty] | Total | 2.8966 | 226.225 | 1165.2375
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 226.225 | total F
|  | 0.21342 | SAIFI=total F/total customers
|  | 1.0993 | SAIDI=total G/total customers
|  | 5.1508 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00012549 | ASUI=1-ASAI
|  | 2896.5656 | ENS=total ENS*1000
|  | 2.7326 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 1.5038 | 1.6457 | 0.545 | 0.81954 | 201.025 | 330.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 2.5381 | 2.7777 | 0.545 | 1.3833 | 201.025 | 558.3875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 4.5725 | 5.0041 | 0.545 | 2.492 | 201.025 | 1005.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.91375 |  | 4.5725 | 5.0041 | 0.5 | 2.2862 | 182.75 | 914.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.91375 |  | 7.5194 | 8.2291 | 0.5 | 3.7597 | 182.75 | 1503.875
[11 empty] | Total | 10.7408 | 968.575 | 4313.5375
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 968.575 | total F
|  | 0.91375 | SAIFI=total F/total customers
|  | 4.0694 | SAIDI=total G/total customers
|  | 4.4535 | CAIDI=SAIDI/SAIFI
|  | 0.99954 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00046454 | ASUI=1-ASAI
|  | 10740.7719 | ENS=total ENS*1000
|  | 10.1328 | AENS=ENS/total customers

## F4_(18-23)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3498.1688
0.1 | 0.025 | 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | B | 27669.975
0.1 | 0.025 |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | C | 4253.4188
0.1 | 0.025 |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | D | 6922.0375
0.1 | 0.025 |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | E | 3498.1688
0.1 | 0.025 |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | F | 13999.85
0.1 | 0.025 |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
0.1 | 0.025 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
| 0.025 |  |  | x former |  |  | 0 | 0 | 0
| 0.025 |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.545 | 0.59541 | 46.2 | 240.35
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.5 | 0.54625 | 42 | 218.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.5 | 0.55188 | 42.75 | 220.75
[11 empty] | Total | 3.4982 | 272.025 | 1408.075
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 272.025 | total F
|  | 0.21252 | SAIFI=total F/total customers
|  | 1.1001 | SAIDI=total G/total customers
|  | 5.1763 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00012558 | ASUI=1-ASAI
|  | 3498.1688 | ENS=total ENS*1000
|  | 2.7329 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.545 | 4.7422 | 227.425 | 1914.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.545 | 4.7422 | 227.425 | 1914.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.545 | 4.7422 | 227.425 | 1914.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.545 | 4.7422 | 227.425 | 1914.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.5 | 4.3506 | 206.75 | 1740.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.5 | 4.3506 | 206.75 | 1740.25
[11 empty] | Total | 27.67 | 1323.2 | 11137.6
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1323.2 | total F
|  | 1.0337 | SAIFI=total F/total customers
|  | 8.7012 | SAIDI=total G/total customers
|  | 8.4172 | CAIDI=SAIDI/SAIFI
|  | 0.99901 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00099329 | ASUI=1-ASAI
|  | 27669.975 | ENS=total ENS*1000
|  | 21.6172 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.545 | 0.73098 | 47.025 | 295.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.545 | 0.72485 | 46.2 | 292.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.545 | 0.73098 | 47.025 | 295.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.545 | 0.73098 | 47.025 | 295.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.5 | 0.665 | 42 | 266
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.5 | 0.67063 | 42.75 | 268.25
[11 empty] | Total | 4.2534 | 272.025 | 1712.075
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 272.025 | total F
|  | 0.21252 | SAIFI=total F/total customers
|  | 1.3376 | SAIDI=total G/total customers
|  | 6.2938 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015269 | ASUI=1-ASAI
|  | 4253.4188 | ENS=total ENS*1000
|  | 3.323 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 1.5138 | 1.4643 | 0.545 | 0.82499 | 227.425 | 333.025
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.545 | 1.3632 | 227.425 | 550.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.545 | 1.3632 | 227.425 | 550.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.545 | 1.3632 | 227.425 | 550.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.5 | 1.2506 | 206.75 | 500.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 1.5138 | 1.4643 | 0.5 | 0.75688 | 206.75 | 302.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
[11 empty] | Total | 6.922 | 1323.2 | 2786.85
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1323.2 | total F
|  | 1.0337 | SAIFI=total F/total customers
|  | 2.1772 | SAIDI=total G/total customers
|  | 2.1061 | CAIDI=SAIDI/SAIFI
|  | 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00024854 | ASUI=1-ASAI
|  | 6922.0375 | ENS=total ENS*1000
|  | 5.4078 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.545 | 0.59541 | 46.2 | 240.35
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.5 | 0.54625 | 42 | 218.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.5 | 0.55188 | 42.75 | 220.75
[11 empty] | Total | 3.4982 | 272.025 | 1408.075
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 272.025 | total F
|  | 0.21252 | SAIFI=total F/total customers
|  | 1.1001 | SAIDI=total G/total customers
|  | 5.1763 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00012558 | ASUI=1-ASAI
|  | 3498.1688 | ENS=total ENS*1000
|  | 2.7329 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 1.5638 | 1.5127 | 0.545 | 0.85224 | 227.425 | 344.025
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 3.5981 | 3.4807 | 0.545 | 1.961 | 227.425 | 791.5875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 3.5981 | 3.4807 | 0.545 | 1.961 | 227.425 | 791.5875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 5.6325 | 5.4486 | 0.545 | 3.0697 | 227.425 | 1239.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 5.6325 | 5.4486 | 0.5 | 2.8162 | 206.75 | 1126.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.0337 |  | 6.6794 | 6.4613 | 0.5 | 3.3397 | 206.75 | 1335.875
[11 empty] | Total | 13.9999 | 1323.2 | 5628.725
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1323.2 | total F
|  | 1.0337 | SAIFI=total F/total customers
|  | 4.3974 | SAIDI=total G/total customers
|  | 4.2539 | CAIDI=SAIDI/SAIFI
|  | 0.9995 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00050199 | ASUI=1-ASAI
|  | 13999.85 | ENS=total ENS*1000
|  | 10.9374 | AENS=ENS/total customers

## F7_(32-37)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3498.225
0.1 | 0.025 | 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | B | 24311.1
0.1 | 0.025 |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | C | 4290.75
0.1 | 0.025 |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | D | 6198.725
0.1 | 0.025 |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | E | 3498.225
0.1 | 0.025 |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | F | 13821.1312
0.1 | 0.025 |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
0.1 | 0.025 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.025 |  |  | Calculation |  |  | 0.21 |  | 1.105 | 5.2619 | 0.545 | 0.60223 | 46.2 | 243.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.105 | 5.2619 | 0.545 | 0.60223 | 46.2 | 243.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.205 |  | 1.09 | 5.3171 | 0.545 | 0.59405 | 45.1 | 239.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.105 | 4.9111 | 0.545 | 0.60223 | 49.5 | 243.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.09 | 4.8444 | 0.5 | 0.545 | 45 | 218
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.105 | 4.9111 | 0.5 | 0.5525 | 45 | 221
[11 empty] | Total | 3.4982 | 277 | 1408.1
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 277 | total F
|  | 0.21641 | SAIFI=total F/total customers
|  | 1.1001 | SAIDI=total G/total customers
|  | 5.0834 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00012558 | ASUI=1-ASAI
|  | 3498.225 | ENS=total ENS*1000
|  | 2.733 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.545 | 4.1665 | 201.3 | 1681.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.545 | 4.1665 | 201.3 | 1681.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.545 | 4.1665 | 201.3 | 1681.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.545 | 4.1665 | 201.3 | 1681.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.5 | 3.8225 | 183 | 1529
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.5 | 3.8225 | 183 | 1529
[11 empty] | Total | 24.3111 | 1171.2 | 9785.6
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1171.2 | total F
|  | 0.915 | SAIFI=total F/total customers
|  | 7.645 | SAIDI=total G/total customers
|  | 8.3552 | CAIDI=SAIDI/SAIFI
|  | 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00087272 | ASUI=1-ASAI
|  | 24311.1 | ENS=total ENS*1000
|  | 18.993 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.545 | 0.72485 | 46.2 | 292.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.545 | 0.72485 | 46.2 | 292.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.205 |  | 1.315 | 6.4146 | 0.545 | 0.71668 | 45.1 | 289.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.375 | 6.1111 | 0.545 | 0.74938 | 49.5 | 302.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.375 | 6.1111 | 0.5 | 0.6875 | 45 | 275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.375 | 6.1111 | 0.5 | 0.6875 | 45 | 275
[11 empty] | Total | 4.2908 | 277 | 1727
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 277 | total F
|  | 0.21641 | SAIFI=total F/total customers
|  | 1.3492 | SAIDI=total G/total customers
|  | 6.2347 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015402 | ASUI=1-ASAI
|  | 4290.75 | ENS=total ENS*1000
|  | 3.3521 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 1.4575 | 1.5929 | 0.545 | 0.79434 | 201.3 | 320.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 1.4575 | 1.5929 | 0.545 | 0.79434 | 201.3 | 320.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 2.445 | 2.6721 | 0.545 | 1.3325 | 201.3 | 537.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 2.445 | 2.6721 | 0.545 | 1.3325 | 201.3 | 537.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 1.445 | 1.5792 | 0.5 | 0.7225 | 183 | 289
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 2.445 | 2.6721 | 0.5 | 1.2225 | 183 | 489
[11 empty] | Total | 6.1987 | 1171.2 | 2495.1
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1171.2 | total F
|  | 0.915 | SAIFI=total F/total customers
|  | 1.9493 | SAIDI=total G/total customers
|  | 2.1304 | CAIDI=SAIDI/SAIFI
|  | 0.99978 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00022252 | ASUI=1-ASAI
|  | 6198.725 | ENS=total ENS*1000
|  | 4.8428 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.105 | 5.2619 | 0.545 | 0.60223 | 46.2 | 243.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.21 |  | 1.105 | 5.2619 | 0.545 | 0.60223 | 46.2 | 243.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.205 |  | 1.09 | 5.3171 | 0.545 | 0.59405 | 45.1 | 239.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.105 | 4.9111 | 0.545 | 0.60223 | 49.5 | 243.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.09 | 4.8444 | 0.5 | 0.545 | 45 | 218
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.225 |  | 1.105 | 4.9111 | 0.5 | 0.5525 | 45 | 221
[11 empty] | Total | 3.4982 | 277 | 1408.1
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 277 | total F
|  | 0.21641 | SAIFI=total F/total customers
|  | 1.1001 | SAIDI=total G/total customers
|  | 5.0834 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00012558 | ASUI=1-ASAI
|  | 3498.225 | ENS=total ENS*1000
|  | 2.733 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 1.5044 | 1.6441 | 0.545 | 0.81988 | 201.3 | 330.9625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 2.5419 | 2.778 | 0.545 | 1.3853 | 201.3 | 559.2125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 4.5762 | 5.0014 | 0.545 | 2.4941 | 201.3 | 1006.775
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 4.5762 | 5.0014 | 0.545 | 2.4941 | 201.3 | 1006.775
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 0.915 |  | 5.6106 | 6.1318 | 0.5 | 2.8053 | 183 | 1122.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.5 | 3.8225 | 183 | 1529
[11 empty] | Total | 13.8211 | 1171.2 | 5554.85
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1171.2 | total F
|  | 0.915 | SAIFI=total F/total customers
|  | 4.3397 | SAIDI=total G/total customers
|  | 4.7429 | CAIDI=SAIDI/SAIFI
|  | 0.9995 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0004954 | ASUI=1-ASAI
|  | 13821.1312 | ENS=total ENS*1000
|  | 10.7978 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 2944.4813 |  | 20518.75 |  | 3564.2313 |  | 4937.5313 |  | 2944.4813 |  | 10023.672
Feeder 3 | 2896.5656 |  | 20134.6938 |  | 3531.8313 |  | 4864.2719 |  | 2896.5656 |  | 10740.7719
Feeder 4 | 3498.169 |  | 27669.98 |  | 4253.419 |  | 6922.038 |  | 3498.169 |  | 13999.85
Feeder 7 | 3498.225 |  | 24311.1 |  | 4290.75 |  | 6198.725 |  | 3498.225 |  | 13821.13
TOTAL | 12837.4409 |  | 92634.5238 |  | 15640.2316 |  | 22922.5662 |  | 12837.4409 |  | 48585.4239
Analytic | 12.8374 |  | 92.6345 |  | 15.6402 |  | 22.9226 |  | 12.8374 |  | 48.5854
Monte Carlo_Code | 12.835 |  | 92.593 |  | 15.525 |  | 22.921 |  | 12.829 |  | 47.666
Deviation | 0.019014 |  | 0.044825 |  | 0.73676 |  | 0.0068325 |  | 0.065752 |  | 1.8924
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 12.835 | 12.838 | 12.826 | 12.831 |  | 945000 | 92.664 | 92.685 | 92.593 | 92.685
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 15.494 | 15.513 | 15.525 | 15.514 |  | 47500 | 22.868 | 22.834 | 22.921 | 22.902
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 12.829 | 12.806 | 12.852 | 12.853 |  | 1140000 | 47.602 | 47.609 | 47.666 | 47.602