## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 285.625
0.025 | 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | B | 1141.875
0.025 |  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | C | 766.875
0.025 |  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | D | 348.125
0.025 |  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045 | [5 empty] | E | 285.625
0.025 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 826.25
0.025 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | Calculation |  |  | 0.07 |  | 0.0725 | 1.0357 | 1 | 0.0725 | 0.07 | 0.0725
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.08375 | 1.1356 | 1.5 | 0.12563 | 0.07375 | 0.08375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.075 |  | 0.0875 | 1.1667 | 1 | 0.0875 | 0.075 | 0.0875
[10 empty] | Total | 0.28563 | 0.21875 | 0.24375
| 3 | total customers
| 26280 | total (customers*8760)
| 0.21875 | total F
| 0.072917 | SAIFI=total F/total customers
| 0.08125 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 9.2751e-06 | ASUI=1-ASAI
| 285.625 | ENS=total ENS*1000
| 95.2083 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.32625 | 3 | 1 | 0.32625 | 0.10875 | 0.32625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.32625 | 3 | 1.5 | 0.48938 | 0.10875 | 0.32625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.32625 | 3 | 1 | 0.32625 | 0.10875 | 0.32625
[10 empty] | Total | 1.1419 | 0.32625 | 0.97875
| 3 | total customers
| 26280 | total (customers*8760)
| 0.32625 | total F
| 0.10875 | SAIFI=total F/total customers
| 0.32625 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.7243e-05 | ASUI=1-ASAI
| 1141.875 | ENS=total ENS*1000
| 380.625 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07 |  | 0.21 | 3 | 1 | 0.21 | 0.07 | 0.21
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.22125 | 3 | 1.5 | 0.33188 | 0.07375 | 0.22125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.075 |  | 0.225 | 3 | 1 | 0.225 | 0.075 | 0.225
[10 empty] | Total | 0.76688 | 0.21875 | 0.65625
| 3 | total customers
| 26280 | total (customers*8760)
| 0.21875 | total F
| 0.072917 | SAIFI=total F/total customers
| 0.21875 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.4971e-05 | ASUI=1-ASAI
| 766.875 | ENS=total ENS*1000
| 255.625 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 18 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | Calculation |  |  | 0.10875 |  | 0.091875 | 0.84483 | 1 | 0.091875 | 0.10875 | 0.091875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | Calculation |  |  | 0.10875 |  | 0.10125 | 0.93103 | 1.5 | 0.15188 | 0.10875 | 0.10125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.10438 | 0.95977 | 1 | 0.10438 | 0.10875 | 0.10438
[10 empty] | Total | 0.34813 | 0.32625 | 0.2975
| 3 | total customers
| 26280 | total (customers*8760)
| 0.32625 | total F
| 0.10875 | SAIFI=total F/total customers
| 0.099167 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.132e-05 | ASUI=1-ASAI
| 348.125 | ENS=total ENS*1000
| 116.0417 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 18 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | Calculation |  |  | 0.10875 |  | 0.14188 | 1.3046 | 1 | 0.14188 | 0.10875 | 0.14188
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | Calculation |  |  | 0.10875 |  | 0.23875 | 2.1954 | 1.5 | 0.35813 | 0.10875 | 0.23875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.32625 | 3 | 1 | 0.32625 | 0.10875 | 0.32625
[10 empty] | Total | 0.82625 | 0.32625 | 0.70688
| 3 | total customers
| 26280 | total (customers*8760)
| 0.32625 | total F
| 0.10875 | SAIFI=total F/total customers
| 0.23563 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.6898e-05 | ASUI=1-ASAI
| 826.25 | ENS=total ENS*1000
| 275.4167 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 241.875
0.025 | 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | B | 967.5
0.025 |  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075 | [5 empty] | C | 645
0.025 |  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | D | 295.625
0.025 |  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625 | [5 empty] | E | 241.875
0.025 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 711.25
0.025 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | Calculation |  |  | 0.0725 |  | 0.083125 | 1.1466 | 1 | 0.083125 | 0.0725 | 0.083125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.086875 | 1.178 | 1 | 0.086875 | 0.07375 | 0.086875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.06875 |  | 0.071875 | 1.0455 | 1 | 0.071875 | 0.06875 | 0.071875
[10 empty] | Total | 0.24188 | 0.215 | 0.24188
| 3 | total customers
| 26280 | total (customers*8760)
| 0.215 | total F
| 0.071667 | SAIFI=total F/total customers
| 0.080625 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 9.2038e-06 | ASUI=1-ASAI
| 241.875 | ENS=total ENS*1000
| 80.625 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
[10 empty] | Total | 0.9675 | 0.3225 | 0.9675
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.3225 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.6815e-05 | ASUI=1-ASAI
| 967.5 | ENS=total ENS*1000
| 322.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.0725 |  | 0.2175 | 3 | 1 | 0.2175 | 0.0725 | 0.2175
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.22125 | 3 | 1 | 0.22125 | 0.07375 | 0.22125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.06875 |  | 0.20625 | 3 | 1 | 0.20625 | 0.06875 | 0.20625
[10 empty] | Total | 0.645 | 0.215 | 0.645
| 3 | total customers
| 26280 | total (customers*8760)
| 0.215 | total F
| 0.071667 | SAIFI=total F/total customers
| 0.215 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.4543e-05 | ASUI=1-ASAI
| 645 | ENS=total ENS*1000
| 215 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 49 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.10063 | 0.93605 | 1 | 0.10063 | 0.1075 | 0.10063
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.10375 | 0.96512 | 1 | 0.10375 | 0.1075 | 0.10375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 47 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.09125 | 0.84884 | 1 | 0.09125 | 0.1075 | 0.09125
[10 empty] | Total | 0.29563 | 0.3225 | 0.29563
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.098542 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.1249e-05 | ASUI=1-ASAI
| 295.625 | ENS=total ENS*1000
| 98.5417 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 49 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.15063 | 1.4012 | 1 | 0.15063 | 0.1075 | 0.15063
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.23813 | 2.2151 | 1 | 0.23813 | 0.1075 | 0.23813
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
[10 empty] | Total | 0.71125 | 0.3225 | 0.71125
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.23708 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.7064e-05 | ASUI=1-ASAI
| 711.25 | ENS=total ENS*1000
| 237.0833 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 271.5625
0.025 | 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375 | [5 empty] | B | 1128.75
0.025 |  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | C | 785.625
0.025 |  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01 | [5 empty] | D | 328.75
0.025 |  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045 | [5 empty] | E | 271.5625
0.025 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 856.875
0.025 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | Calculation |  |  | 0.07375 |  | 0.074375 | 1.0085 | 1 | 0.074375 | 0.07375 | 0.074375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.0775 |  | 0.085625 | 1.1048 | 1 | 0.085625 | 0.0775 | 0.085625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.07375 |  | 0.074375 | 1.0085 | 1.5 | 0.11156 | 0.07375 | 0.074375
[10 empty] | Total | 0.27156 | 0.225 | 0.23438
| 3 | total customers
| 26280 | total (customers*8760)
| 0.225 | total F
| 0.075 | SAIFI=total F/total customers
| 0.078125 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 8.9184e-06 | ASUI=1-ASAI
| 271.5625 | ENS=total ENS*1000
| 90.5208 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1.5 | 0.48375 | 0.1075 | 0.3225
[10 empty] | Total | 1.1288 | 0.3225 | 0.9675
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.3225 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.6815e-05 | ASUI=1-ASAI
| 1128.75 | ENS=total ENS*1000
| 376.25 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.22125 | 3 | 1 | 0.22125 | 0.07375 | 0.22125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.0775 |  | 0.2325 | 3 | 1 | 0.2325 | 0.0775 | 0.2325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.07375 |  | 0.22125 | 3 | 1.5 | 0.33188 | 0.07375 | 0.22125
[10 empty] | Total | 0.78563 | 0.225 | 0.675
| 3 | total customers
| 26280 | total (customers*8760)
| 0.225 | total F
| 0.075 | SAIFI=total F/total customers
| 0.225 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.5685e-05 | ASUI=1-ASAI
| 785.625 | ENS=total ENS*1000
| 261.875 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 55 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.09125 | 0.84884 | 1 | 0.09125 | 0.1075 | 0.09125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.10063 | 0.93605 | 1 | 0.10063 | 0.1075 | 0.10063
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.09125 | 0.84884 | 1.5 | 0.13687 | 0.1075 | 0.09125
[10 empty] | Total | 0.32875 | 0.3225 | 0.28313
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.094375 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.0773e-05 | ASUI=1-ASAI
| 328.75 | ENS=total ENS*1000
| 109.5833 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 55 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.13813 | 1.2849 | 1 | 0.13813 | 0.1075 | 0.13813
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.235 | 2.186 | 1 | 0.235 | 0.1075 | 0.235
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1.5 | 0.48375 | 0.1075 | 0.3225
[10 empty] | Total | 0.85688 | 0.3225 | 0.69563
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.23188 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.647e-05 | ASUI=1-ASAI
| 856.875 | ENS=total ENS*1000
| 285.625 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 2 | 285.63 |  | 1141.9 |  | 766.88 |  | 348.13 |  | 285.63 |  | 826.25
Feeder 5 | 241.875 |  | 967.5 |  | 645 |  | 295.625 |  | 241.875 |  | 711.25
Feeder 6 | 271.5625 |  | 1128.75 |  | 785.625 |  | 328.75 |  | 271.5625 |  | 856.875
TOTAL | 799.0675 |  | 3238.15 |  | 2197.505 |  | 972.505 |  | 799.0675 |  | 2394.375
Analytic | 0.79907 |  | 3.2382 |  | 2.1975 |  | 0.9725 |  | 0.79907 |  | 2.3944
Monte Carlo_Code | 0.79891 |  | 3.2377 |  | 2.1963 |  | 0.9723 |  | 0.79712 |  | 2.3937
Deviation | 0.01971 |  | 0.013897 |  | 0.054835 |  | 0.02108 |  | 0.24372 |  | 0.028191
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 0.79837 | 0.79849 | 0.79953 | 0.79891 |  | 945000 | 3.2377 | 3.2398 | 3.2395 | 3.2351
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 2.1963 | 2.1953 | 2.1941 | 2.1977 |  | 47500 | 0.9723 | 0.97252 | 0.97266 | 0.97389
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 0.80083 | 0.79712 | 0.79962 | 0.80088 |  | 1140000 | 2.3956 | 2.3937 | 2.3917 | 2.3949