## F1_(6-7)
[7 empty] | CASE A | [6 empty] | ENS
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1003.2625
0.05 | 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | B | 6899.375
0.05 |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | C | 1387.1375
0.05 |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | D | 2209.875
0.05 |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | E | 1003.2625
0.05 |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | F | 6899.375
0.05 |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
0.05 |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0 | 0
0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.2125 | 3.3448 | 0.415 | 0.50319 | 3.625 | 12.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.205 | 3.3241 | 0.415 | 0.50008 | 3.625 | 12.05
[10 empty] | Total | 1.0033 | 7.25 | 24.175
| 20 | total customers
| 175200 | total (customers*8760)
| 7.25 | total F
| 0.3625 | SAIFI=total F/total customers
| 1.2087 | SAIDI=total G/total customers
| 3.3345 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013799 | ASUI=1-ASAI
| 1003.2625 | ENS=total ENS*1000
| 50.1631 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.415 | 3.4497 | 11.375 | 83.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.415 | 3.4497 | 11.375 | 83.125
[10 empty] | Total | 6.8994 | 22.75 | 166.25
| 20 | total customers
| 175200 | total (customers*8760)
| 22.75 | total F
| 1.1375 | SAIFI=total F/total customers
| 8.3125 | SAIDI=total G/total customers
| 7.3077 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094892 | ASUI=1-ASAI
| 6899.375 | ENS=total ENS*1000
| 344.9688 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.675 | 4.6207 | 0.415 | 0.69512 | 3.625 | 16.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.6675 | 4.6 | 0.415 | 0.69201 | 3.625 | 16.675
[10 empty] | Total | 1.3871 | 7.25 | 33.425
| 20 | total customers
| 175200 | total (customers*8760)
| 7.25 | total F
| 0.3625 | SAIFI=total F/total customers
| 1.6712 | SAIDI=total G/total customers
| 4.6103 | CAIDI=SAIDI/SAIFI
| 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00019078 | ASUI=1-ASAI
| 1387.1375 | ENS=total ENS*1000
| 69.3569 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 2.6625 | 2.3407 | 0.415 | 1.1049 | 11.375 | 26.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 2.6625 | 2.3407 | 0.415 | 1.1049 | 11.375 | 26.625
[10 empty] | Total | 2.2099 | 22.75 | 53.25
| 20 | total customers
| 175200 | total (customers*8760)
| 22.75 | total F
| 1.1375 | SAIFI=total F/total customers
| 2.6625 | SAIDI=total G/total customers
| 2.3407 | CAIDI=SAIDI/SAIFI
| 0.9997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00030394 | ASUI=1-ASAI
| 2209.875 | ENS=total ENS*1000
| 110.4937 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.2125 | 3.3448 | 0.415 | 0.50319 | 3.625 | 12.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.205 | 3.3241 | 0.415 | 0.50008 | 3.625 | 12.05
[10 empty] | Total | 1.0033 | 7.25 | 24.175
| 20 | total customers
| 175200 | total (customers*8760)
| 7.25 | total F
| 0.3625 | SAIFI=total F/total customers
| 1.2087 | SAIDI=total G/total customers
| 3.3345 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013799 | ASUI=1-ASAI
| 1003.2625 | ENS=total ENS*1000
| 50.1631 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.415 | 3.4497 | 11.375 | 83.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.415 | 3.4497 | 11.375 | 83.125
[10 empty] | Total | 6.8994 | 22.75 | 166.25
| 20 | total customers
| 175200 | total (customers*8760)
| 22.75 | total F
| 1.1375 | SAIFI=total F/total customers
| 8.3125 | SAIDI=total G/total customers
| 7.3077 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094892 | ASUI=1-ASAI
| 6899.375 | ENS=total ENS*1000
| 344.9688 | AENS=ENS/total customers

## F3_(16-17)
[7 empty] | CASE A | [6 empty] | ENS
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 987.7
0.05 | 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | B | 6874.475
0.05 |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | C | 1440.05
0.05 |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | D | 2184.975
0.05 |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | E | 987.7
0.05 |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | F | 6874.475
0.05 |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
0.05 |  |  | 30 | 0.6 | 0.05 | 0.03 | 0 | 0
0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.2012 | 3.4819 | 0.415 | 0.49852 | 3.45 | 12.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.1787 | 3.4167 | 0.415 | 0.48918 | 3.45 | 11.7875
[10 empty] | Total | 0.9877 | 6.9 | 23.8
| 20 | total customers
| 175200 | total (customers*8760)
| 6.9 | total F
| 0.345 | SAIFI=total F/total customers
| 1.19 | SAIDI=total G/total customers
| 3.4493 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013584 | ASUI=1-ASAI
| 987.7 | ENS=total ENS*1000
| 49.385 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.415 | 3.4372 | 11.275 | 82.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.415 | 3.4372 | 11.275 | 82.825
[10 empty] | Total | 6.8745 | 22.55 | 165.65
| 20 | total customers
| 175200 | total (customers*8760)
| 22.55 | total F
| 1.1275 | SAIFI=total F/total customers
| 8.2825 | SAIDI=total G/total customers
| 7.3459 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094549 | ASUI=1-ASAI
| 6874.475 | ENS=total ENS*1000
| 343.7237 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.735 | 5.029 | 0.415 | 0.72002 | 3.45 | 17.35
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.735 | 5.029 | 0.415 | 0.72002 | 3.45 | 17.35
[10 empty] | Total | 1.44 | 6.9 | 34.7
| 20 | total customers
| 175200 | total (customers*8760)
| 6.9 | total F
| 0.345 | SAIFI=total F/total customers
| 1.735 | SAIDI=total G/total customers
| 5.029 | CAIDI=SAIDI/SAIFI
| 0.9998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00019806 | ASUI=1-ASAI
| 1440.05 | ENS=total ENS*1000
| 72.0025 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 2.6325 | 2.3348 | 0.415 | 1.0925 | 11.275 | 26.325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 2.6325 | 2.3348 | 0.415 | 1.0925 | 11.275 | 26.325
[10 empty] | Total | 2.185 | 22.55 | 52.65
| 20 | total customers
| 175200 | total (customers*8760)
| 22.55 | total F
| 1.1275 | SAIFI=total F/total customers
| 2.6325 | SAIDI=total G/total customers
| 2.3348 | CAIDI=SAIDI/SAIFI
| 0.9997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00030051 | ASUI=1-ASAI
| 2184.975 | ENS=total ENS*1000
| 109.2487 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.2012 | 3.4819 | 0.415 | 0.49852 | 3.45 | 12.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.1787 | 3.4167 | 0.415 | 0.48918 | 3.45 | 11.7875
[10 empty] | Total | 0.9877 | 6.9 | 23.8
| 20 | total customers
| 175200 | total (customers*8760)
| 6.9 | total F
| 0.345 | SAIFI=total F/total customers
| 1.19 | SAIDI=total G/total customers
| 3.4493 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013584 | ASUI=1-ASAI
| 987.7 | ENS=total ENS*1000
| 49.385 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.415 | 3.4372 | 11.275 | 82.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.415 | 3.4372 | 11.275 | 82.825
[10 empty] | Total | 6.8745 | 22.55 | 165.65
| 20 | total customers
| 175200 | total (customers*8760)
| 22.55 | total F
| 1.1275 | SAIFI=total F/total customers
| 8.2825 | SAIDI=total G/total customers
| 7.3459 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094549 | ASUI=1-ASAI
| 6874.475 | ENS=total ENS*1000
| 343.7237 | AENS=ENS/total customers

## F4_(24-25)
[7 empty] | CASE A | [6 empty] | ENS
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 992.8875
0.05 | 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | B | 7804.075
0.05 |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | C | 1387.1375
0.05 |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | D | 2243.075
0.05 |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | E | 992.8875
0.05 |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | F | 7804.075
0.05 |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
0.05 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
0.05 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.415 | 0.50111 | 3.275 | 12.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.415 | 0.49178 | 3.2 | 11.85
[10 empty] | Total | 0.99289 | 6.475 | 23.925
| 20 | total customers
| 175200 | total (customers*8760)
| 6.475 | total F
| 0.32375 | SAIFI=total F/total customers
| 1.1963 | SAIDI=total G/total customers
| 3.695 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013656 | ASUI=1-ASAI
| 992.8875 | ENS=total ENS*1000
| 49.6444 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.415 | 3.902 | 12.675 | 94.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.415 | 3.902 | 12.675 | 94.025
[10 empty] | Total | 7.8041 | 25.35 | 188.05
| 20 | total customers
| 175200 | total (customers*8760)
| 25.35 | total F
| 1.2675 | SAIFI=total F/total customers
| 9.4025 | SAIDI=total G/total customers
| 7.4181 | CAIDI=SAIDI/SAIFI
| 0.99893 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010733 | ASUI=1-ASAI
| 7804.075 | ENS=total ENS*1000
| 390.2037 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.415 | 0.69824 | 3.275 | 16.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.415 | 0.6889 | 3.2 | 16.6
[10 empty] | Total | 1.3871 | 6.475 | 33.425
| 20 | total customers
| 175200 | total (customers*8760)
| 6.475 | total F
| 0.32375 | SAIFI=total F/total customers
| 1.6713 | SAIDI=total G/total customers
| 5.1622 | CAIDI=SAIDI/SAIFI
| 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00019078 | ASUI=1-ASAI
| 1387.1375 | ENS=total ENS*1000
| 69.3569 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.415 | 1.1215 | 12.675 | 27.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.415 | 1.1215 | 12.675 | 27.025
[10 empty] | Total | 2.2431 | 25.35 | 54.05
| 20 | total customers
| 175200 | total (customers*8760)
| 25.35 | total F
| 1.2675 | SAIFI=total F/total customers
| 2.7025 | SAIDI=total G/total customers
| 2.1321 | CAIDI=SAIDI/SAIFI
| 0.99969 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0003085 | ASUI=1-ASAI
| 2243.075 | ENS=total ENS*1000
| 112.1537 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.415 | 0.50111 | 3.275 | 12.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.415 | 0.49178 | 3.2 | 11.85
[10 empty] | Total | 0.99289 | 6.475 | 23.925
| 20 | total customers
| 175200 | total (customers*8760)
| 6.475 | total F
| 0.32375 | SAIFI=total F/total customers
| 1.1963 | SAIDI=total G/total customers
| 3.695 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013656 | ASUI=1-ASAI
| 992.8875 | ENS=total ENS*1000
| 49.6444 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.415 | 3.902 | 12.675 | 94.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.415 | 3.902 | 12.675 | 94.025
[10 empty] | Total | 7.8041 | 25.35 | 188.05
| 20 | total customers
| 175200 | total (customers*8760)
| 25.35 | total F
| 1.2675 | SAIFI=total F/total customers
| 9.4025 | SAIDI=total G/total customers
| 7.4181 | CAIDI=SAIDI/SAIFI
| 0.99893 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010733 | ASUI=1-ASAI
| 7804.075 | ENS=total ENS*1000
| 390.2037 | AENS=ENS/total customers

## F7_(38)
[7 empty] | CASE A | [6 empty] | ENS
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 489.7
0.05 | 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | B | 3440.35
0.05 |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | C | 726.25
0.05 |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | D | 1095.6
0.05 |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | E | 489.7
0.05 |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | F | 3440.35
0.05 |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 66 | 0.8 | 0.05 | 0.04 | 0 | 0
0.05 |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.18 | 3.3714 | 0.415 | 0.4897 | 3.5 | 11.8
[10 empty] | Total | 0.4897 | 3.5 | 11.8
| 10 | total customers
| 87600 | total (customers*8760)
| 3.5 | total F
| 0.35 | SAIFI=total F/total customers
| 1.18 | SAIDI=total G/total customers
| 3.3714 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001347 | ASUI=1-ASAI
| 489.7 | ENS=total ENS*1000
| 48.97 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.415 | 3.4403 | 11.3 | 82.9
[10 empty] | Total | 3.4403 | 11.3 | 82.9
| 10 | total customers
| 87600 | total (customers*8760)
| 11.3 | total F
| 1.13 | SAIFI=total F/total customers
| 8.29 | SAIDI=total G/total customers
| 7.3363 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094635 | ASUI=1-ASAI
| 3440.35 | ENS=total ENS*1000
| 344.035 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.75 | 5 | 0.415 | 0.72625 | 3.5 | 17.5
[10 empty] | Total | 0.72625 | 3.5 | 17.5
| 10 | total customers
| 87600 | total (customers*8760)
| 3.5 | total F
| 0.35 | SAIFI=total F/total customers
| 1.75 | SAIDI=total G/total customers
| 5 | CAIDI=SAIDI/SAIFI
| 0.9998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00019977 | ASUI=1-ASAI
| 726.25 | ENS=total ENS*1000
| 72.625 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 2.64 | 2.3363 | 0.415 | 1.0956 | 11.3 | 26.4
[10 empty] | Total | 1.0956 | 11.3 | 26.4
| 10 | total customers
| 87600 | total (customers*8760)
| 11.3 | total F
| 1.13 | SAIFI=total F/total customers
| 2.64 | SAIDI=total G/total customers
| 2.3363 | CAIDI=SAIDI/SAIFI
| 0.9997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00030137 | ASUI=1-ASAI
| 1095.6 | ENS=total ENS*1000
| 109.56 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.18 | 3.3714 | 0.415 | 0.4897 | 3.5 | 11.8
[10 empty] | Total | 0.4897 | 3.5 | 11.8
| 10 | total customers
| 87600 | total (customers*8760)
| 3.5 | total F
| 0.35 | SAIFI=total F/total customers
| 1.18 | SAIDI=total G/total customers
| 3.3714 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001347 | ASUI=1-ASAI
| 489.7 | ENS=total ENS*1000
| 48.97 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.415 | 3.4403 | 11.3 | 82.9
[10 empty] | Total | 3.4403 | 11.3 | 82.9
| 10 | total customers
| 87600 | total (customers*8760)
| 11.3 | total F
| 1.13 | SAIFI=total F/total customers
| 8.29 | SAIDI=total G/total customers
| 7.3363 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094635 | ASUI=1-ASAI
| 3440.35 | ENS=total ENS*1000
| 344.035 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 1003.2625 |  | 6899.375 |  | 1387.1375 |  | 2209.875 |  | 1003.2625 |  | 6899.375
Feeder 3 | 987.7 |  | 6874.475 |  | 1440.05 |  | 2184.975 |  | 987.7 |  | 6874.475
Feeder 4 | 992.8875 |  | 7804.075 |  | 1387.1375 |  | 2243.075 |  | 992.8875 |  | 7804.075
Feeder 7 | 489.7 |  | 3440.35 |  | 726.25 |  | 1095.6 |  | 489.7 |  | 3440.35
TOTAL | 3473.55 |  | 25018.275 |  | 4940.575 |  | 7733.525 |  | 3473.55 |  | 25018.275
Analytic | 3.4736 |  | 25.0183 |  | 4.9406 |  | 7.7335 |  | 3.4736 |  | 25.0183
Monte Carlo_Code | 3.4728 |  | 25.014 |  | 4.8114 |  | 7.7321 |  | 3.4725 |  | 25.014
Deviation | 0.021592 |  | 0.017088 |  | 2.6146 |  | 0.018426 |  | 0.030228 |  | 0.017088
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 3.4761 | 3.4705 | 3.4698 | 3.4728 |  | 945000 | 24.976 | 25.028 | 25.035 | 25.014
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 4.8078 | 4.8047 | 4.8114 | 4.8071 |  | 47500 | 7.7321 | 7.7401 | 7.7337 | 7.7387
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 3.4663 | 3.4752 | 3.4765 | 3.4725 |  | 1140000 | 25.036 | 25 | 25.011 | 25.014