## F1_(1-5)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3208.9625
0.1 | 0.05 | 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | B | 22277.5
0.1 | 0.05 |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | C | 4448.4625
0.1 | 0.05 |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | D | 5398.3125
0.1 | 0.05 |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | E | 3208.9625
0.1 | 0.05 |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | F | 11039.0938
0.1 | 0.05 |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
0.1 | 0.05 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | Calculation |  |  | 0.315 |  | 1.1825 | 3.754 | 0.545 | 0.64446 | 69.3 | 260.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3225 |  | 1.205 | 3.7364 | 0.545 | 0.65673 | 70.95 | 265.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.1825 | 3.754 | 0.545 | 0.64446 | 69.3 | 260.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3625 |  | 1.2125 | 3.3448 | 0.545 | 0.66081 | 79.75 | 266.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3625 |  | 1.205 | 3.3241 | 0.5 | 0.6025 | 72.5 | 241
[11 empty] | Total | 3.209 | 361.8 | 1293.15
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 361.8 | total F
|  | 0.335 | SAIFI=total F/total customers
|  | 1.1974 | SAIDI=total G/total customers
|  | 3.5742 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00013669 | ASUI=1-ASAI
|  | 3208.9625 | ENS=total ENS*1000
|  | 2.9713 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.545 | 4.5303 | 250.25 | 1828.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.545 | 4.5303 | 250.25 | 1828.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.545 | 4.5303 | 250.25 | 1828.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.545 | 4.5303 | 250.25 | 1828.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.5 | 4.1562 | 227.5 | 1662.5
[11 empty] | Total | 22.2775 | 1228.5 | 8977.5
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1228.5 | total F
|  | 1.1375 | SAIFI=total F/total customers
|  | 8.3125 | SAIDI=total G/total customers
|  | 7.3077 | CAIDI=SAIDI/SAIFI
|  | 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00094892 | ASUI=1-ASAI
|  | 22277.5 | ENS=total ENS*1000
|  | 20.6273 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.645 | 5.2222 | 0.545 | 0.89653 | 69.3 | 361.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3225 |  | 1.6675 | 5.1705 | 0.545 | 0.90879 | 70.95 | 366.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.645 | 5.2222 | 0.545 | 0.89653 | 69.3 | 361.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3625 |  | 1.675 | 4.6207 | 0.545 | 0.91288 | 79.75 | 368.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3625 |  | 1.6675 | 4.6 | 0.5 | 0.83375 | 72.5 | 333.5
[11 empty] | Total | 4.4485 | 361.8 | 1792.65
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 361.8 | total F
|  | 0.335 | SAIFI=total F/total customers
|  | 1.6599 | SAIDI=total G/total customers
|  | 4.9548 | CAIDI=SAIDI/SAIFI
|  | 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00018948 | ASUI=1-ASAI
|  | 4448.4625 | ENS=total ENS*1000
|  | 4.1189 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 1.5938 | 1.4011 | 0.545 | 0.86859 | 250.25 | 350.625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 1.6125 | 1.4176 | 0.545 | 0.87881 | 250.25 | 354.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 1.5938 | 1.4011 | 0.545 | 0.86859 | 250.25 | 350.625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 2.6625 | 2.3407 | 0.545 | 1.4511 | 250.25 | 585.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 2.6625 | 2.3407 | 0.5 | 1.3312 | 227.5 | 532.5
[11 empty] | Total | 5.3983 | 1228.5 | 2174.25
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1228.5 | total F
|  | 1.1375 | SAIFI=total F/total customers
|  | 2.0132 | SAIDI=total G/total customers
|  | 1.7698 | CAIDI=SAIDI/SAIFI
|  | 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00022982 | ASUI=1-ASAI
|  | 5398.3125 | ENS=total ENS*1000
|  | 4.9984 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.1825 | 3.754 | 0.545 | 0.64446 | 69.3 | 260.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3225 |  | 1.205 | 3.7364 | 0.545 | 0.65673 | 70.95 | 265.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.1825 | 3.754 | 0.545 | 0.64446 | 69.3 | 260.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3625 |  | 1.2125 | 3.3448 | 0.545 | 0.66081 | 79.75 | 266.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3625 |  | 1.205 | 3.3241 | 0.5 | 0.6025 | 72.5 | 241
[11 empty] | Total | 3.209 | 361.8 | 1293.15
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 361.8 | total F
|  | 0.335 | SAIFI=total F/total customers
|  | 1.1974 | SAIDI=total G/total customers
|  | 3.5742 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00013669 | ASUI=1-ASAI
|  | 3208.9625 | ENS=total ENS*1000
|  | 2.9713 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 1.6875 | 1.4835 | 0.545 | 0.91969 | 250.25 | 371.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 2.8312 | 2.489 | 0.545 | 1.543 | 250.25 | 622.875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 3.9562 | 3.478 | 0.545 | 2.1562 | 250.25 | 870.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 6.1437 | 5.4011 | 0.545 | 3.3483 | 250.25 | 1351.625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1375 |  | 6.1437 | 5.4011 | 0.5 | 3.0719 | 227.5 | 1228.75
[11 empty] | Total | 11.0391 | 1228.5 | 4444.875
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1228.5 | total F
|  | 1.1375 | SAIFI=total F/total customers
|  | 4.1156 | SAIDI=total G/total customers
|  | 3.6181 | CAIDI=SAIDI/SAIFI
|  | 0.99953 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00046982 | ASUI=1-ASAI
|  | 11039.0938 | ENS=total ENS*1000
|  | 10.2214 | AENS=ENS/total customers

## F3_(11-15)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3158.1312
0.1 | 0.05 | 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | B | 21824.3875
0.1 | 0.05 |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | C | 4428.6625
0.1 | 0.05 |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | D | 5310.2938
0.1 | 0.05 |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | E | 3158.1312
0.1 | 0.05 |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | F | 11710.0438
0.1 | 0.05 |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
0.1 | 0.05 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | Calculation |  |  | 0.3175 |  | 1.2087 | 3.8071 | 0.545 | 0.65877 | 69.85 | 265.925
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.2012 | 3.8135 | 0.545 | 0.65468 | 69.3 | 264.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.2012 | 3.8135 | 0.545 | 0.65468 | 69.3 | 264.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.345 |  | 1.1787 | 3.4167 | 0.5 | 0.58937 | 69 | 235.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.345 |  | 1.2012 | 3.4819 | 0.5 | 0.60062 | 69 | 240.25
[11 empty] | Total | 3.1581 | 346.45 | 1270.475
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 346.45 | total F
|  | 0.32684 | SAIFI=total F/total customers
|  | 1.1986 | SAIDI=total G/total customers
|  | 3.6671 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00013682 | ASUI=1-ASAI
|  | 3158.1312 | ENS=total ENS*1000
|  | 2.9794 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.545 | 4.514 | 248.05 | 1822.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.545 | 4.514 | 248.05 | 1822.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.545 | 4.514 | 248.05 | 1822.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.5 | 4.1413 | 225.5 | 1656.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.5 | 4.1413 | 225.5 | 1656.5
[11 empty] | Total | 21.8244 | 1195.15 | 8779.45
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1195.15 | total F
|  | 1.1275 | SAIFI=total F/total customers
|  | 8.2825 | SAIDI=total G/total customers
|  | 7.3459 | CAIDI=SAIDI/SAIFI
|  | 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00094549 | ASUI=1-ASAI
|  | 21824.3875 | ENS=total ENS*1000
|  | 20.589 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3175 |  | 1.6525 | 5.2047 | 0.545 | 0.90061 | 69.85 | 363.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.645 | 5.2222 | 0.545 | 0.89653 | 69.3 | 361.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.645 | 5.2222 | 0.545 | 0.89653 | 69.3 | 361.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.345 |  | 1.735 | 5.029 | 0.5 | 0.8675 | 69 | 347
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.345 |  | 1.735 | 5.029 | 0.5 | 0.8675 | 69 | 347
[11 empty] | Total | 4.4287 | 346.45 | 1781.35
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 346.45 | total F
|  | 0.32684 | SAIFI=total F/total customers
|  | 1.6805 | SAIDI=total G/total customers
|  | 5.1417 | CAIDI=SAIDI/SAIFI
|  | 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00019184 | ASUI=1-ASAI
|  | 4428.6625 | ENS=total ENS*1000
|  | 4.178 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 1.6138 | 1.4313 | 0.545 | 0.87949 | 248.05 | 355.025
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 1.6075 | 1.4257 | 0.545 | 0.87609 | 248.05 | 353.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 2.6325 | 2.3348 | 0.545 | 1.4347 | 248.05 | 579.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 2.6325 | 2.3348 | 0.5 | 1.3162 | 225.5 | 526.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 1.6075 | 1.4257 | 0.5 | 0.80375 | 225.5 | 321.5
[11 empty] | Total | 5.3103 | 1195.15 | 2135.825
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1195.15 | total F
|  | 1.1275 | SAIFI=total F/total customers
|  | 2.0149 | SAIDI=total G/total customers
|  | 1.7871 | CAIDI=SAIDI/SAIFI
|  | 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00023001 | ASUI=1-ASAI
|  | 5310.2938 | ENS=total ENS*1000
|  | 5.0097 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3175 |  | 1.2087 | 3.8071 | 0.545 | 0.65877 | 69.85 | 265.925
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.2012 | 3.8135 | 0.545 | 0.65468 | 69.3 | 264.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.315 |  | 1.2012 | 3.8135 | 0.545 | 0.65468 | 69.3 | 264.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.345 |  | 1.1787 | 3.4167 | 0.5 | 0.58937 | 69 | 235.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.345 |  | 1.2012 | 3.4819 | 0.5 | 0.60062 | 69 | 240.25
[11 empty] | Total | 3.1581 | 346.45 | 1270.475
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 346.45 | total F
|  | 0.32684 | SAIFI=total F/total customers
|  | 1.1986 | SAIDI=total G/total customers
|  | 3.6671 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00013682 | ASUI=1-ASAI
|  | 3158.1312 | ENS=total ENS*1000
|  | 2.9794 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 1.7075 | 1.5144 | 0.545 | 0.93059 | 248.05 | 375.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 2.8262 | 2.5067 | 0.545 | 1.5403 | 248.05 | 621.775
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 4.995 | 4.4302 | 0.545 | 2.7223 | 248.05 | 1098.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.1275 |  | 4.995 | 4.4302 | 0.5 | 2.4975 | 225.5 | 999
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.1275 |  | 8.0388 | 7.1297 | 0.5 | 4.0194 | 225.5 | 1607.75
[11 empty] | Total | 11.71 | 1195.15 | 4703.075
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1195.15 | total F
|  | 1.1275 | SAIFI=total F/total customers
|  | 4.4369 | SAIDI=total G/total customers
|  | 3.9351 | CAIDI=SAIDI/SAIFI
|  | 0.99949 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00050649 | ASUI=1-ASAI
|  | 11710.0438 | ENS=total ENS*1000
|  | 11.0472 | AENS=ENS/total customers

## F4_(18-23)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3816.3375
0.1 | 0.05 | 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | B | 29899.95
0.1 | 0.05 |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | C | 5326.8375
0.1 | 0.05 |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | D | 7522.825
0.1 | 0.05 |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | E | 3816.3375
0.1 | 0.05 |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | F | 15289.7
0.1 | 0.05 |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
0.1 | 0.05 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
| 0.05 |  |  | x former |  |  | 0 | 0 | 0
| 0.05 |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.545 | 0.64583 | 70.4 | 260.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.5 | 0.5925 | 64 | 237
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.5 | 0.60375 | 65.5 | 241.5
[11 empty] | Total | 3.8163 | 416.05 | 1536.15
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 416.05 | total F
|  | 0.32504 | SAIFI=total F/total customers
|  | 1.2001 | SAIDI=total G/total customers
|  | 3.6922 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.000137 | ASUI=1-ASAI
|  | 3816.3375 | ENS=total ENS*1000
|  | 2.9815 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.545 | 5.1244 | 278.85 | 2068.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.545 | 5.1244 | 278.85 | 2068.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.545 | 5.1244 | 278.85 | 2068.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.545 | 5.1244 | 278.85 | 2068.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.5 | 4.7012 | 253.5 | 1880.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.5 | 4.7012 | 253.5 | 1880.5
[11 empty] | Total | 29.9 | 1622.4 | 12035.2
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1622.4 | total F
|  | 1.2675 | SAIFI=total F/total customers
|  | 9.4025 | SAIDI=total G/total customers
|  | 7.4181 | CAIDI=SAIDI/SAIFI
|  | 0.99893 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0010733 | ASUI=1-ASAI
|  | 29899.95 | ENS=total ENS*1000
|  | 23.3593 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.545 | 0.91696 | 72.05 | 370.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.545 | 0.9047 | 70.4 | 365.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.545 | 0.91696 | 72.05 | 370.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.545 | 0.91696 | 72.05 | 370.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.5 | 0.83 | 64 | 332
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.5 | 0.84125 | 65.5 | 336.5
[11 empty] | Total | 5.3268 | 416.05 | 2144.15
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 416.05 | total F
|  | 0.32504 | SAIFI=total F/total customers
|  | 1.6751 | SAIDI=total G/total customers
|  | 5.1536 | CAIDI=SAIDI/SAIFI
|  | 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00019122 | ASUI=1-ASAI
|  | 5326.8375 | ENS=total ENS*1000
|  | 4.1616 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 1.6775 | 1.3235 | 0.545 | 0.91424 | 278.85 | 369.05
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.545 | 1.4729 | 278.85 | 594.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.545 | 1.4729 | 278.85 | 594.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.545 | 1.4729 | 278.85 | 594.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.5 | 1.3512 | 253.5 | 540.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 1.6775 | 1.3235 | 0.5 | 0.83875 | 253.5 | 335.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
[11 empty] | Total | 7.5228 | 1622.4 | 3028.7
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1622.4 | total F
|  | 1.2675 | SAIFI=total F/total customers
|  | 2.3662 | SAIDI=total G/total customers
|  | 1.8668 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00027011 | ASUI=1-ASAI
|  | 7522.825 | ENS=total ENS*1000
|  | 5.8772 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.545 | 0.64583 | 70.4 | 260.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.5 | 0.5925 | 64 | 237
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.5 | 0.60375 | 65.5 | 241.5
[11 empty] | Total | 3.8163 | 416.05 | 1536.15
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 416.05 | total F
|  | 0.32504 | SAIFI=total F/total customers
|  | 1.2001 | SAIDI=total G/total customers
|  | 3.6922 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.000137 | ASUI=1-ASAI
|  | 3816.3375 | ENS=total ENS*1000
|  | 2.9815 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 1.7775 | 1.4024 | 0.545 | 0.96874 | 278.85 | 391.05
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 3.9462 | 3.1134 | 0.545 | 2.1507 | 278.85 | 868.175
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 3.9462 | 3.1134 | 0.545 | 2.1507 | 278.85 | 868.175
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 6.115 | 4.8245 | 0.545 | 3.3327 | 278.85 | 1345.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 6.115 | 4.8245 | 0.5 | 3.0575 | 253.5 | 1223
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.2675 |  | 7.2588 | 5.7268 | 0.5 | 3.6294 | 253.5 | 1451.75
[11 empty] | Total | 15.2897 | 1622.4 | 6147.45
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1622.4 | total F
|  | 1.2675 | SAIFI=total F/total customers
|  | 4.8027 | SAIDI=total G/total customers
|  | 3.7891 | CAIDI=SAIDI/SAIFI
|  | 0.99945 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00054825 | ASUI=1-ASAI
|  | 15289.7 | ENS=total ENS*1000
|  | 11.9451 | AENS=ENS/total customers

## F7_(32-37)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3816.45
0.1 | 0.05 | 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | B | 26362.2
0.1 | 0.05 |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | C | 5401.5
0.1 | 0.05 |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | D | 6752.95
0.1 | 0.05 |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | E | 3816.45
0.1 | 0.05 |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | F | 15134.0125
0.1 | 0.05 |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
0.1 | 0.05 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.05 |  |  | Calculation |  |  | 0.32 |  | 1.21 | 3.7812 | 0.545 | 0.65945 | 70.4 | 266.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.21 | 3.7812 | 0.545 | 0.65945 | 70.4 | 266.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.31 |  | 1.18 | 3.8065 | 0.545 | 0.6431 | 68.2 | 259.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.21 | 3.4571 | 0.545 | 0.65945 | 77 | 266.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.18 | 3.3714 | 0.5 | 0.59 | 70 | 236
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.21 | 3.4571 | 0.5 | 0.605 | 70 | 242
[11 empty] | Total | 3.8164 | 426 | 1536.2
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 426 | total F
|  | 0.33281 | SAIFI=total F/total customers
|  | 1.2002 | SAIDI=total G/total customers
|  | 3.6061 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.000137 | ASUI=1-ASAI
|  | 3816.45 | ENS=total ENS*1000
|  | 2.9816 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.545 | 4.518 | 248.6 | 1823.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.545 | 4.518 | 248.6 | 1823.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.545 | 4.518 | 248.6 | 1823.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.545 | 4.518 | 248.6 | 1823.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.5 | 4.145 | 226 | 1658
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.5 | 4.145 | 226 | 1658
[11 empty] | Total | 26.3622 | 1446.4 | 10611.2
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1446.4 | total F
|  | 1.13 | SAIFI=total F/total customers
|  | 8.29 | SAIDI=total G/total customers
|  | 7.3363 | CAIDI=SAIDI/SAIFI
|  | 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00094635 | ASUI=1-ASAI
|  | 26362.2 | ENS=total ENS*1000
|  | 20.5955 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.545 | 0.9047 | 70.4 | 365.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.545 | 0.9047 | 70.4 | 365.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.31 |  | 1.63 | 5.2581 | 0.545 | 0.88835 | 68.2 | 358.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.75 | 5 | 0.545 | 0.95375 | 77 | 385
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.75 | 5 | 0.5 | 0.875 | 70 | 350
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.75 | 5 | 0.5 | 0.875 | 70 | 350
[11 empty] | Total | 5.4015 | 426 | 2174
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 426 | total F
|  | 0.33281 | SAIFI=total F/total customers
|  | 1.6984 | SAIDI=total G/total customers
|  | 5.1033 | CAIDI=SAIDI/SAIFI
|  | 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00019389 | ASUI=1-ASAI
|  | 5401.5 | ENS=total ENS*1000
|  | 4.2199 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 1.615 | 1.4292 | 0.545 | 0.88018 | 248.6 | 355.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 1.615 | 1.4292 | 0.545 | 0.88018 | 248.6 | 355.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 2.64 | 2.3363 | 0.545 | 1.4388 | 248.6 | 580.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 2.64 | 2.3363 | 0.545 | 1.4388 | 248.6 | 580.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 1.59 | 1.4071 | 0.5 | 0.795 | 226 | 318
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 2.64 | 2.3363 | 0.5 | 1.32 | 226 | 528
[11 empty] | Total | 6.7529 | 1446.4 | 2718.2
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1446.4 | total F
|  | 1.13 | SAIFI=total F/total customers
|  | 2.1236 | SAIDI=total G/total customers
|  | 1.8793 | CAIDI=SAIDI/SAIFI
|  | 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00024242 | ASUI=1-ASAI
|  | 6752.95 | ENS=total ENS*1000
|  | 5.2757 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.21 | 3.7812 | 0.545 | 0.65945 | 70.4 | 266.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.32 |  | 1.21 | 3.7812 | 0.545 | 0.65945 | 70.4 | 266.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.31 |  | 1.18 | 3.8065 | 0.545 | 0.6431 | 68.2 | 259.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.21 | 3.4571 | 0.545 | 0.65945 | 77 | 266.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.18 | 3.3714 | 0.5 | 0.59 | 70 | 236
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.35 |  | 1.21 | 3.4571 | 0.5 | 0.605 | 70 | 242
[11 empty] | Total | 3.8164 | 426 | 1536.2
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 426 | total F
|  | 0.33281 | SAIFI=total F/total customers
|  | 1.2002 | SAIDI=total G/total customers
|  | 3.6061 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.000137 | ASUI=1-ASAI
|  | 3816.45 | ENS=total ENS*1000
|  | 2.9816 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 1.7088 | 1.5122 | 0.545 | 0.93127 | 248.6 | 375.925
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 2.8337 | 2.5077 | 0.545 | 1.5444 | 248.6 | 623.425
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 5.0025 | 4.427 | 0.545 | 2.7264 | 248.6 | 1100.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 5.0025 | 4.427 | 0.545 | 2.7264 | 248.6 | 1100.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.13 |  | 6.1212 | 5.417 | 0.5 | 3.0606 | 226 | 1224.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.5 | 4.145 | 226 | 1658
[11 empty] | Total | 15.134 | 1446.4 | 6082.7
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1446.4 | total F
|  | 1.13 | SAIFI=total F/total customers
|  | 4.7521 | SAIDI=total G/total customers
|  | 4.2054 | CAIDI=SAIDI/SAIFI
|  | 0.99946 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00054248 | ASUI=1-ASAI
|  | 15134.0125 | ENS=total ENS*1000
|  | 11.8234 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 3208.9625 |  | 22277.5 |  | 4448.4625 |  | 5398.3125 |  | 3208.9625 |  | 11039.094
Feeder 3 | 3158.1312 |  | 21824.3875 |  | 4428.6625 |  | 5310.2937 |  | 3158.1312 |  | 11710.0438
Feeder 4 | 3816.338 |  | 29899.95 |  | 5326.838 |  | 7522.825 |  | 3816.338 |  | 15289.7
Feeder 7 | 3816.45 |  | 26362.2 |  | 5401.5 |  | 6752.95 |  | 3816.45 |  | 15134.01
TOTAL | 13999.8818 |  | 100364.0375 |  | 19605.463 |  | 24984.3813 |  | 13999.8818 |  | 53172.8478
Analytic | 13.9999 |  | 100.364 |  | 19.6055 |  | 24.9844 |  | 13.9999 |  | 53.1728
Monte Carlo_Code | 13.993 |  | 100.32 |  | 19.356 |  | 24.98 |  | 13.995 |  | 52.22
Deviation | 0.049156 |  | 0.043878 |  | 1.2724 |  | 0.017536 |  | 0.03487 |  | 1.792
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 13.993 | 14.008 | 13.99 | 13.989 |  | 945000 | 100.32 | 100.37 | 100.41 | 100.37
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 19.354 | 19.347 | 19.356 | 19.336 |  | 47500 | 25.017 | 24.968 | 24.971 | 24.98
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 14.029 | 14.006 | 13.994 | 13.995 |  | 1140000 | 52.22 | 52.197 | 52.203 | 52.216