## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 571.25
0.05 | 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | B | 2283.75
0.05 |  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | C | 1533.75
0.05 |  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | D | 696.25
0.05 |  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09 | [5 empty] | E | 571.25
0.05 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 1652.5
0.05 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | Calculation |  |  | 0.14 |  | 0.145 | 1.0357 | 1 | 0.145 | 0.14 | 0.145
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.1675 | 1.1356 | 1.5 | 0.25125 | 0.1475 | 0.1675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.15 |  | 0.175 | 1.1667 | 1 | 0.175 | 0.15 | 0.175
[10 empty] | Total | 0.57125 | 0.4375 | 0.4875
| 3 | total customers
| 26280 | total (customers*8760)
| 0.4375 | total F
| 0.14583 | SAIFI=total F/total customers
| 0.1625 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.855e-05 | ASUI=1-ASAI
| 571.25 | ENS=total ENS*1000
| 190.4167 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1 | 0.6525 | 0.2175 | 0.6525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1.5 | 0.97875 | 0.2175 | 0.6525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1 | 0.6525 | 0.2175 | 0.6525
[10 empty] | Total | 2.2838 | 0.6525 | 1.9575
| 3 | total customers
| 26280 | total (customers*8760)
| 0.6525 | total F
| 0.2175 | SAIFI=total F/total customers
| 0.6525 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.4486e-05 | ASUI=1-ASAI
| 2283.75 | ENS=total ENS*1000
| 761.25 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.14 |  | 0.42 | 3 | 1 | 0.42 | 0.14 | 0.42
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.4425 | 3 | 1.5 | 0.66375 | 0.1475 | 0.4425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.15 |  | 0.45 | 3 | 1 | 0.45 | 0.15 | 0.45
[10 empty] | Total | 1.5338 | 0.4375 | 1.3125
| 3 | total customers
| 26280 | total (customers*8760)
| 0.4375 | total F
| 0.14583 | SAIFI=total F/total customers
| 0.4375 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.9943e-05 | ASUI=1-ASAI
| 1533.75 | ENS=total ENS*1000
| 511.25 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 18 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | Calculation |  |  | 0.2175 |  | 0.18375 | 0.84483 | 1 | 0.18375 | 0.2175 | 0.18375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | Calculation |  |  | 0.2175 |  | 0.2025 | 0.93103 | 1.5 | 0.30375 | 0.2175 | 0.2025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.20875 | 0.95977 | 1 | 0.20875 | 0.2175 | 0.20875
[10 empty] | Total | 0.69625 | 0.6525 | 0.595
| 3 | total customers
| 26280 | total (customers*8760)
| 0.6525 | total F
| 0.2175 | SAIFI=total F/total customers
| 0.19833 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.2641e-05 | ASUI=1-ASAI
| 696.25 | ENS=total ENS*1000
| 232.0833 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 18 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | Calculation |  |  | 0.2175 |  | 0.28375 | 1.3046 | 1 | 0.28375 | 0.2175 | 0.28375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | Calculation |  |  | 0.2175 |  | 0.4775 | 2.1954 | 1.5 | 0.71625 | 0.2175 | 0.4775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1 | 0.6525 | 0.2175 | 0.6525
[10 empty] | Total | 1.6525 | 0.6525 | 1.4138
| 3 | total customers
| 26280 | total (customers*8760)
| 0.6525 | total F
| 0.2175 | SAIFI=total F/total customers
| 0.47125 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.3796e-05 | ASUI=1-ASAI
| 1652.5 | ENS=total ENS*1000
| 550.8333 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 483.75
0.05 | 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | B | 1935
0.05 |  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015 | [5 empty] | C | 1290
0.05 |  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | D | 591.25
0.05 |  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125 | [5 empty] | E | 483.75
0.05 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 1422.5
0.05 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | Calculation |  |  | 0.145 |  | 0.16625 | 1.1466 | 1 | 0.16625 | 0.145 | 0.16625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.17375 | 1.178 | 1 | 0.17375 | 0.1475 | 0.17375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.1375 |  | 0.14375 | 1.0455 | 1 | 0.14375 | 0.1375 | 0.14375
[10 empty] | Total | 0.48375 | 0.43 | 0.48375
| 3 | total customers
| 26280 | total (customers*8760)
| 0.43 | total F
| 0.14333 | SAIFI=total F/total customers
| 0.16125 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.8408e-05 | ASUI=1-ASAI
| 483.75 | ENS=total ENS*1000
| 161.25 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
[10 empty] | Total | 1.935 | 0.645 | 1.935
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.645 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.363e-05 | ASUI=1-ASAI
| 1935 | ENS=total ENS*1000
| 645 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.145 |  | 0.435 | 3 | 1 | 0.435 | 0.145 | 0.435
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.4425 | 3 | 1 | 0.4425 | 0.1475 | 0.4425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.1375 |  | 0.4125 | 3 | 1 | 0.4125 | 0.1375 | 0.4125
[10 empty] | Total | 1.29 | 0.43 | 1.29
| 3 | total customers
| 26280 | total (customers*8760)
| 0.43 | total F
| 0.14333 | SAIFI=total F/total customers
| 0.43 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.9087e-05 | ASUI=1-ASAI
| 1290 | ENS=total ENS*1000
| 430 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 49 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.20125 | 0.93605 | 1 | 0.20125 | 0.215 | 0.20125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.2075 | 0.96512 | 1 | 0.2075 | 0.215 | 0.2075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 47 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.1825 | 0.84884 | 1 | 0.1825 | 0.215 | 0.1825
[10 empty] | Total | 0.59125 | 0.645 | 0.59125
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.19708 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.2498e-05 | ASUI=1-ASAI
| 591.25 | ENS=total ENS*1000
| 197.0833 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 49 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.30125 | 1.4012 | 1 | 0.30125 | 0.215 | 0.30125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.47625 | 2.2151 | 1 | 0.47625 | 0.215 | 0.47625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
[10 empty] | Total | 1.4225 | 0.645 | 1.4225
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.47417 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.4129e-05 | ASUI=1-ASAI
| 1422.5 | ENS=total ENS*1000
| 474.1667 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 543.125
0.05 | 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875 | [5 empty] | B | 2257.5
0.05 |  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | C | 1571.25
0.05 |  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02 | [5 empty] | D | 657.5
0.05 |  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09 | [5 empty] | E | 543.125
0.05 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 1713.75
0.05 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | Calculation |  |  | 0.1475 |  | 0.14875 | 1.0085 | 1 | 0.14875 | 0.1475 | 0.14875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.155 |  | 0.17125 | 1.1048 | 1 | 0.17125 | 0.155 | 0.17125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.1475 |  | 0.14875 | 1.0085 | 1.5 | 0.22312 | 0.1475 | 0.14875
[10 empty] | Total | 0.54312 | 0.45 | 0.46875
| 3 | total customers
| 26280 | total (customers*8760)
| 0.45 | total F
| 0.15 | SAIFI=total F/total customers
| 0.15625 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.7837e-05 | ASUI=1-ASAI
| 543.125 | ENS=total ENS*1000
| 181.0417 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1.5 | 0.9675 | 0.215 | 0.645
[10 empty] | Total | 2.2575 | 0.645 | 1.935
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.645 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.363e-05 | ASUI=1-ASAI
| 2257.5 | ENS=total ENS*1000
| 752.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.4425 | 3 | 1 | 0.4425 | 0.1475 | 0.4425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.155 |  | 0.465 | 3 | 1 | 0.465 | 0.155 | 0.465
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.1475 |  | 0.4425 | 3 | 1.5 | 0.66375 | 0.1475 | 0.4425
[10 empty] | Total | 1.5713 | 0.45 | 1.35
| 3 | total customers
| 26280 | total (customers*8760)
| 0.45 | total F
| 0.15 | SAIFI=total F/total customers
| 0.45 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.137e-05 | ASUI=1-ASAI
| 1571.25 | ENS=total ENS*1000
| 523.75 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 55 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.1825 | 0.84884 | 1 | 0.1825 | 0.215 | 0.1825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.20125 | 0.93605 | 1 | 0.20125 | 0.215 | 0.20125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.1825 | 0.84884 | 1.5 | 0.27375 | 0.215 | 0.1825
[10 empty] | Total | 0.6575 | 0.645 | 0.56625
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.18875 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.1547e-05 | ASUI=1-ASAI
| 657.5 | ENS=total ENS*1000
| 219.1667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 55 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.27625 | 1.2849 | 1 | 0.27625 | 0.215 | 0.27625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.47 | 2.186 | 1 | 0.47 | 0.215 | 0.47
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1.5 | 0.9675 | 0.215 | 0.645
[10 empty] | Total | 1.7138 | 0.645 | 1.3913
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.46375 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.2939e-05 | ASUI=1-ASAI
| 1713.75 | ENS=total ENS*1000
| 571.25 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 2 | 571.25 |  | 2283.8 |  | 1533.8 |  | 696.25 |  | 571.25 |  | 1652.5
Feeder 5 | 483.75 |  | 1935 |  | 1290 |  | 591.25 |  | 483.75 |  | 1422.5
Feeder 6 | 543.125 |  | 2257.5 |  | 1571.25 |  | 657.5 |  | 543.125 |  | 1713.75
TOTAL | 1598.125 |  | 6476.3 |  | 4395.05 |  | 1945 |  | 1598.125 |  | 4788.75
Analytic | 1.5981 |  | 6.4763 |  | 4.3951 |  | 1.945 |  | 1.5981 |  | 4.7888
Monte Carlo_Code | 1.5965 |  | 6.4625 |  | 4.3899 |  | 1.9448 |  | 1.5926 |  | 4.7879
Deviation | 0.10168 |  | 0.21308 |  | 0.11718 |  | 0.010283 |  | 0.34572 |  | 0.01775
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 1.5965 | 1.6016 | 1.5987 | 1.5991 |  | 945000 | 6.4625 | 6.4859 | 6.5155 | 6.4789
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 4.3882 | 4.3899 | 4.4108 | 4.4018 |  | 47500 | 1.9491 | 1.9441 | 1.9448 | 1.9467
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 1.6001 | 1.5926 | 1.5996 | 1.5999 |  | 1140000 | 4.7693 | 4.7879 | 4.8357 | 4.8003