## F1_(6-7)
[7 empty] | CASE A | [6 empty] | ENS
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1089.8938
0.075 | 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | B | 7444.0625
0.075 |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 1665.7062
0.075 |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 2381.0625
0.075 |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | E | 1089.8938
0.075 |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | F | 7444.0625
0.075 |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
0.075 |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0 | 0
0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3188 | 2.6709 | 0.415 | 0.54728 | 4.9375 | 13.1875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3075 | 2.6481 | 0.415 | 0.54261 | 4.9375 | 13.075
[10 empty] | Total | 1.0899 | 9.875 | 26.2625
| 20 | total customers
| 175200 | total (customers*8760)
| 9.875 | total F
| 0.49375 | SAIFI=total F/total customers
| 1.3131 | SAIDI=total G/total customers
| 2.6595 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001499 | ASUI=1-ASAI
| 1089.8938 | ENS=total ENS*1000
| 54.4947 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.415 | 3.722 | 13.5625 | 89.6875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.415 | 3.722 | 13.5625 | 89.6875
[10 empty] | Total | 7.4441 | 27.125 | 179.375
| 20 | total customers
| 175200 | total (customers*8760)
| 27.125 | total F
| 1.3563 | SAIFI=total F/total customers
| 8.9688 | SAIDI=total G/total customers
| 6.6129 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010238 | ASUI=1-ASAI
| 7444.0625 | ENS=total ENS*1000
| 372.2031 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 2.0125 | 4.0759 | 0.415 | 0.83519 | 4.9375 | 20.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 2.0012 | 4.0532 | 0.415 | 0.83052 | 4.9375 | 20.0125
[10 empty] | Total | 1.6657 | 9.875 | 40.1375
| 20 | total customers
| 175200 | total (customers*8760)
| 9.875 | total F
| 0.49375 | SAIFI=total F/total customers
| 2.0069 | SAIDI=total G/total customers
| 4.0646 | CAIDI=SAIDI/SAIFI
| 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0002291 | ASUI=1-ASAI
| 1665.7062 | ENS=total ENS*1000
| 83.2853 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 2.8687 | 2.1152 | 0.415 | 1.1905 | 13.5625 | 28.6875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 2.8687 | 2.1152 | 0.415 | 1.1905 | 13.5625 | 28.6875
[10 empty] | Total | 2.3811 | 27.125 | 57.375
| 20 | total customers
| 175200 | total (customers*8760)
| 27.125 | total F
| 1.3563 | SAIFI=total F/total customers
| 2.8687 | SAIDI=total G/total customers
| 2.1152 | CAIDI=SAIDI/SAIFI
| 0.99967 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00032748 | ASUI=1-ASAI
| 2381.0625 | ENS=total ENS*1000
| 119.0531 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3188 | 2.6709 | 0.415 | 0.54728 | 4.9375 | 13.1875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3075 | 2.6481 | 0.415 | 0.54261 | 4.9375 | 13.075
[10 empty] | Total | 1.0899 | 9.875 | 26.2625
| 20 | total customers
| 175200 | total (customers*8760)
| 9.875 | total F
| 0.49375 | SAIFI=total F/total customers
| 1.3131 | SAIDI=total G/total customers
| 2.6595 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001499 | ASUI=1-ASAI
| 1089.8938 | ENS=total ENS*1000
| 54.4947 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.415 | 3.722 | 13.5625 | 89.6875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.415 | 3.722 | 13.5625 | 89.6875
[10 empty] | Total | 7.4441 | 27.125 | 179.375
| 20 | total customers
| 175200 | total (customers*8760)
| 27.125 | total F
| 1.3563 | SAIFI=total F/total customers
| 8.9688 | SAIDI=total G/total customers
| 6.6129 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010238 | ASUI=1-ASAI
| 7444.0625 | ENS=total ENS*1000
| 372.2031 | AENS=ENS/total customers

## F3_(16-17)
[7 empty] | CASE A | [6 empty] | ENS
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1066.55
0.075 | 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | B | 7406.7125
0.075 |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | C | 1745.075
0.075 |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 2343.7125
0.075 |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | E | 1066.55
0.075 |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | F | 7406.7125
0.075 |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
0.075 |  |  | 30 | 0.6 | 0.075 | 0.045 | 0 | 0
0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.3019 | 2.7848 | 0.415 | 0.54028 | 4.675 | 13.0187
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.2681 | 2.7126 | 0.415 | 0.52627 | 4.675 | 12.6812
[10 empty] | Total | 1.0665 | 9.35 | 25.7
| 20 | total customers
| 175200 | total (customers*8760)
| 9.35 | total F
| 0.4675 | SAIFI=total F/total customers
| 1.285 | SAIDI=total G/total customers
| 2.7487 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014669 | ASUI=1-ASAI
| 1066.55 | ENS=total ENS*1000
| 53.3275 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.415 | 3.7034 | 13.4125 | 89.2375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.415 | 3.7034 | 13.4125 | 89.2375
[10 empty] | Total | 7.4067 | 26.825 | 178.475
| 20 | total customers
| 175200 | total (customers*8760)
| 26.825 | total F
| 1.3413 | SAIFI=total F/total customers
| 8.9238 | SAIDI=total G/total customers
| 6.6533 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010187 | ASUI=1-ASAI
| 7406.7125 | ENS=total ENS*1000
| 370.3356 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 2.1025 | 4.4973 | 0.415 | 0.87254 | 4.675 | 21.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 2.1025 | 4.4973 | 0.415 | 0.87254 | 4.675 | 21.025
[10 empty] | Total | 1.7451 | 9.35 | 42.05
| 20 | total customers
| 175200 | total (customers*8760)
| 9.35 | total F
| 0.4675 | SAIFI=total F/total customers
| 2.1025 | SAIDI=total G/total customers
| 4.4973 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00024001 | ASUI=1-ASAI
| 1745.075 | ENS=total ENS*1000
| 87.2537 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 2.8237 | 2.1053 | 0.415 | 1.1719 | 13.4125 | 28.2375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 2.8237 | 2.1053 | 0.415 | 1.1719 | 13.4125 | 28.2375
[10 empty] | Total | 2.3437 | 26.825 | 56.475
| 20 | total customers
| 175200 | total (customers*8760)
| 26.825 | total F
| 1.3413 | SAIFI=total F/total customers
| 2.8237 | SAIDI=total G/total customers
| 2.1053 | CAIDI=SAIDI/SAIFI
| 0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00032235 | ASUI=1-ASAI
| 2343.7125 | ENS=total ENS*1000
| 117.1856 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.3019 | 2.7848 | 0.415 | 0.54028 | 4.675 | 13.0187
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.2681 | 2.7126 | 0.415 | 0.52627 | 4.675 | 12.6812
[10 empty] | Total | 1.0665 | 9.35 | 25.7
| 20 | total customers
| 175200 | total (customers*8760)
| 9.35 | total F
| 0.4675 | SAIFI=total F/total customers
| 1.285 | SAIDI=total G/total customers
| 2.7487 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014669 | ASUI=1-ASAI
| 1066.55 | ENS=total ENS*1000
| 53.3275 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.415 | 3.7034 | 13.4125 | 89.2375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.415 | 3.7034 | 13.4125 | 89.2375
[10 empty] | Total | 7.4067 | 26.825 | 178.475
| 20 | total customers
| 175200 | total (customers*8760)
| 26.825 | total F
| 1.3413 | SAIFI=total F/total customers
| 8.9238 | SAIDI=total G/total customers
| 6.6533 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010187 | ASUI=1-ASAI
| 7406.7125 | ENS=total ENS*1000
| 370.3356 | AENS=ENS/total customers

## F4_(24-25)
[7 empty] | CASE A | [6 empty] | ENS
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1074.3312
0.075 | 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | B | 8386.1125
0.075 |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 1665.7062
0.075 |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 2410.1125
0.075 |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | E | 1074.3312
0.075 |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | F | 8386.1125
0.075 |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
0.075 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
0.075 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.415 | 0.54417 | 4.4125 | 13.1125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.415 | 0.53016 | 4.3 | 12.775
[10 empty] | Total | 1.0743 | 8.7125 | 25.8875
| 20 | total customers
| 175200 | total (customers*8760)
| 8.7125 | total F
| 0.43562 | SAIFI=total F/total customers
| 1.2944 | SAIDI=total G/total customers
| 2.9713 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014776 | ASUI=1-ASAI
| 1074.3312 | ENS=total ENS*1000
| 53.7166 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.415 | 4.1931 | 15.0125 | 101.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.415 | 4.1931 | 15.0125 | 101.0375
[10 empty] | Total | 8.3861 | 30.025 | 202.075
| 20 | total customers
| 175200 | total (customers*8760)
| 30.025 | total F
| 1.5013 | SAIFI=total F/total customers
| 10.1037 | SAIDI=total G/total customers
| 6.7302 | CAIDI=SAIDI/SAIFI
| 0.99885 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0011534 | ASUI=1-ASAI
| 8386.1125 | ENS=total ENS*1000
| 419.3056 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.415 | 0.83986 | 4.4125 | 20.2375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.415 | 0.82585 | 4.3 | 19.9
[10 empty] | Total | 1.6657 | 8.7125 | 40.1375
| 20 | total customers
| 175200 | total (customers*8760)
| 8.7125 | total F
| 0.43562 | SAIFI=total F/total customers
| 2.0069 | SAIDI=total G/total customers
| 4.6069 | CAIDI=SAIDI/SAIFI
| 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0002291 | ASUI=1-ASAI
| 1665.7062 | ENS=total ENS*1000
| 83.2853 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.415 | 1.2051 | 15.0125 | 29.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.415 | 1.2051 | 15.0125 | 29.0375
[10 empty] | Total | 2.4101 | 30.025 | 58.075
| 20 | total customers
| 175200 | total (customers*8760)
| 30.025 | total F
| 1.5013 | SAIFI=total F/total customers
| 2.9037 | SAIDI=total G/total customers
| 1.9342 | CAIDI=SAIDI/SAIFI
| 0.99967 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00033148 | ASUI=1-ASAI
| 2410.1125 | ENS=total ENS*1000
| 120.5056 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.415 | 0.54417 | 4.4125 | 13.1125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.415 | 0.53016 | 4.3 | 12.775
[10 empty] | Total | 1.0743 | 8.7125 | 25.8875
| 20 | total customers
| 175200 | total (customers*8760)
| 8.7125 | total F
| 0.43562 | SAIFI=total F/total customers
| 1.2944 | SAIDI=total G/total customers
| 2.9713 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014776 | ASUI=1-ASAI
| 1074.3312 | ENS=total ENS*1000
| 53.7166 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.415 | 4.1931 | 15.0125 | 101.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.415 | 4.1931 | 15.0125 | 101.0375
[10 empty] | Total | 8.3861 | 30.025 | 202.075
| 20 | total customers
| 175200 | total (customers*8760)
| 30.025 | total F
| 1.5013 | SAIFI=total F/total customers
| 10.1037 | SAIDI=total G/total customers
| 6.7302 | CAIDI=SAIDI/SAIFI
| 0.99885 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0011534 | ASUI=1-ASAI
| 8386.1125 | ENS=total ENS*1000
| 419.3056 | AENS=ENS/total customers

## F7_(38)
[7 empty] | CASE A | [6 empty] | ENS
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 527.05
0.075 | 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | B | 3708.025
0.075 |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | C | 881.875
0.075 |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | D | 1176.525
0.075 |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | E | 527.05
0.075 |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | F | 3708.025
0.075 |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 66 | 0.8 | 0.075 | 0.06 | 0 | 0
0.075 |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.27 | 2.6737 | 0.415 | 0.52705 | 4.75 | 12.7
[10 empty] | Total | 0.52705 | 4.75 | 12.7
| 10 | total customers
| 87600 | total (customers*8760)
| 4.75 | total F
| 0.475 | SAIFI=total F/total customers
| 1.27 | SAIDI=total G/total customers
| 2.6737 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014498 | ASUI=1-ASAI
| 527.05 | ENS=total ENS*1000
| 52.705 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.415 | 3.708 | 13.45 | 89.35
[10 empty] | Total | 3.708 | 13.45 | 89.35
| 10 | total customers
| 87600 | total (customers*8760)
| 13.45 | total F
| 1.345 | SAIFI=total F/total customers
| 8.935 | SAIDI=total G/total customers
| 6.6431 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00102 | ASUI=1-ASAI
| 3708.025 | ENS=total ENS*1000
| 370.8025 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 2.125 | 4.4737 | 0.415 | 0.88187 | 4.75 | 21.25
[10 empty] | Total | 0.88187 | 4.75 | 21.25
| 10 | total customers
| 87600 | total (customers*8760)
| 4.75 | total F
| 0.475 | SAIFI=total F/total customers
| 2.125 | SAIDI=total G/total customers
| 4.4737 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00024258 | ASUI=1-ASAI
| 881.875 | ENS=total ENS*1000
| 88.1875 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 2.835 | 2.1078 | 0.415 | 1.1765 | 13.45 | 28.35
[10 empty] | Total | 1.1765 | 13.45 | 28.35
| 10 | total customers
| 87600 | total (customers*8760)
| 13.45 | total F
| 1.345 | SAIFI=total F/total customers
| 2.835 | SAIDI=total G/total customers
| 2.1078 | CAIDI=SAIDI/SAIFI
| 0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00032363 | ASUI=1-ASAI
| 1176.525 | ENS=total ENS*1000
| 117.6525 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.27 | 2.6737 | 0.415 | 0.52705 | 4.75 | 12.7
[10 empty] | Total | 0.52705 | 4.75 | 12.7
| 10 | total customers
| 87600 | total (customers*8760)
| 4.75 | total F
| 0.475 | SAIFI=total F/total customers
| 1.27 | SAIDI=total G/total customers
| 2.6737 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014498 | ASUI=1-ASAI
| 527.05 | ENS=total ENS*1000
| 52.705 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.415 | 3.708 | 13.45 | 89.35
[10 empty] | Total | 3.708 | 13.45 | 89.35
| 10 | total customers
| 87600 | total (customers*8760)
| 13.45 | total F
| 1.345 | SAIFI=total F/total customers
| 8.935 | SAIDI=total G/total customers
| 6.6431 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00102 | ASUI=1-ASAI
| 3708.025 | ENS=total ENS*1000
| 370.8025 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 1089.8937 | 20 | 7444.0625 | 20 | 1665.7062 | 20 | 2381.0625 | 20 | 1089.8937 | 20 | 7444.0625 | 20
Feeder 3 | 1066.55 | 20 | 7406.7125 | 20 | 1745.075 | 20 | 2343.7125 | 20 | 1066.55 | 20 | 7406.7125 | 20
Feeder 4 | 1074.3312 | 20 | 8386.1125 | 20 | 1665.7062 | 20 | 2410.1125 | 20 | 1074.3312 | 20 | 8386.1125 | 20
Feeder 7 | 527.05 | 10 | 3708.025 | 10 | 881.875 | 10 | 1176.525 | 10 | 527.05 | 10 | 3708.025 | 10
TOTAL | 3757.825 | 70 | 26944.9125 | 70 | 5958.3625 | 70 | 8311.4125 | 70 | 3757.825 | 70 | 26944.9125 | 70
Analytic | 3.7578 |  | 26.9449 |  | 5.9584 |  | 8.3114 |  | 3.7578 |  | 26.9449
Monte Carlo_Code | 3.7551 |  | 26.937 |  | 5.7623 |  | 8.3061 |  | 3.7574 |  | 26.91
Deviation | 0.072515 |  | 0.029365 |  | 3.2905 |  | 0.063918 |  | 0.01131 |  | 0.12957
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 3.7791 | 3.7551 | 3.7796 | 3.7625 |  | 945000 | 26.9765 | 26.9641 | 26.9559 | 26.937
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 5.7622 | 5.7519 | 5.7623 | 5.7612 |  | 47500 | 8.3577 | 8.3199 | 8.2674 | 8.3061
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 3.7812 | 3.7574 | 3.769 | 3.7572 |  | 1140000 | 26.91 | 26.9834 | 26.9881 | 26.9712