## F1_(1-5)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3473.4438
0.1 | 0.075 | 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | B | 24036.25
0.1 | 0.075 |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 5332.6938
0.1 | 0.075 |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 5859.0938
0.1 | 0.075 |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | E | 3473.4438
0.1 | 0.075 |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | F | 12054.5156
0.1 | 0.075 |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
0.1 | 0.075 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | Calculation |  |  | 0.4225 |  | 1.2737 | 3.0148 | 0.545 | 0.69419 | 92.95 | 280.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43375 |  | 1.3075 | 3.0144 | 0.545 | 0.71259 | 95.425 | 287.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.2737 | 3.0148 | 0.545 | 0.69419 | 92.95 | 280.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.49375 |  | 1.3188 | 2.6709 | 0.545 | 0.71872 | 108.625 | 290.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.49375 |  | 1.3075 | 2.6481 | 0.5 | 0.65375 | 98.75 | 261.5
[11 empty] | Total | 3.4734 | 488.7 | 1399.725
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 488.7 | total F
|  | 0.4525 | SAIFI=total F/total customers
|  | 1.296 | SAIDI=total G/total customers
|  | 2.8642 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014795 | ASUI=1-ASAI
|  | 3473.4438 | ENS=total ENS*1000
|  | 3.2162 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.545 | 4.888 | 298.375 | 1973.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.545 | 4.888 | 298.375 | 1973.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.545 | 4.888 | 298.375 | 1973.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.545 | 4.888 | 298.375 | 1973.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.5 | 4.4844 | 271.25 | 1793.75
[11 empty] | Total | 24.0363 | 1464.75 | 9686.25
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1464.75 | total F
|  | 1.3563 | SAIFI=total F/total customers
|  | 8.9688 | SAIDI=total G/total customers
|  | 6.6129 | CAIDI=SAIDI/SAIFI
|  | 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0010238 | ASUI=1-ASAI
|  | 24036.25 | ENS=total ENS*1000
|  | 22.2558 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.9675 | 4.6568 | 0.545 | 1.0723 | 92.95 | 432.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43375 |  | 2.0012 | 4.6138 | 0.545 | 1.0907 | 95.425 | 440.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.9675 | 4.6568 | 0.545 | 1.0723 | 92.95 | 432.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.49375 |  | 2.0125 | 4.0759 | 0.545 | 1.0968 | 108.625 | 442.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.49375 |  | 2.0012 | 4.0532 | 0.5 | 1.0006 | 98.75 | 400.25
[11 empty] | Total | 5.3327 | 488.7 | 2148.975
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 488.7 | total F
|  | 0.4525 | SAIFI=total F/total customers
|  | 1.9898 | SAIDI=total G/total customers
|  | 4.3973 | CAIDI=SAIDI/SAIFI
|  | 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00022715 | ASUI=1-ASAI
|  | 5332.6938 | ENS=total ENS*1000
|  | 4.9377 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 1.7406 | 1.2834 | 0.545 | 0.94864 | 298.375 | 382.9375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 1.7688 | 1.3041 | 0.545 | 0.96397 | 298.375 | 389.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 1.7406 | 1.2834 | 0.545 | 0.94864 | 298.375 | 382.9375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 2.8687 | 2.1152 | 0.545 | 1.5635 | 298.375 | 631.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 2.8687 | 2.1152 | 0.5 | 1.4344 | 271.25 | 573.75
[11 empty] | Total | 5.8591 | 1464.75 | 2359.875
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1464.75 | total F
|  | 1.3563 | SAIFI=total F/total customers
|  | 2.1851 | SAIDI=total G/total customers
|  | 1.6111 | CAIDI=SAIDI/SAIFI
|  | 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00024944 | ASUI=1-ASAI
|  | 5859.0938 | ENS=total ENS*1000
|  | 5.4251 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.2737 | 3.0148 | 0.545 | 0.69419 | 92.95 | 280.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43375 |  | 1.3075 | 3.0144 | 0.545 | 0.71259 | 95.425 | 287.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.2737 | 3.0148 | 0.545 | 0.69419 | 92.95 | 280.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.49375 |  | 1.3188 | 2.6709 | 0.545 | 0.71872 | 108.625 | 290.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.49375 |  | 1.3075 | 2.6481 | 0.5 | 0.65375 | 98.75 | 261.5
[11 empty] | Total | 3.4734 | 488.7 | 1399.725
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 488.7 | total F
|  | 0.4525 | SAIFI=total F/total customers
|  | 1.296 | SAIDI=total G/total customers
|  | 2.8642 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014795 | ASUI=1-ASAI
|  | 3473.4438 | ENS=total ENS*1000
|  | 3.2162 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 1.8813 | 1.3871 | 0.545 | 1.0253 | 298.375 | 413.875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 3.1219 | 2.3018 | 0.545 | 1.7014 | 298.375 | 686.8125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 4.3344 | 3.1959 | 0.545 | 2.3622 | 298.375 | 953.5625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 6.6656 | 4.9147 | 0.545 | 3.6328 | 298.375 | 1466.4375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3563 |  | 6.6656 | 4.9147 | 0.5 | 3.3328 | 271.25 | 1333.125
[11 empty] | Total | 12.0545 | 1464.75 | 4853.8125
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1464.75 | total F
|  | 1.3563 | SAIFI=total F/total customers
|  | 4.4943 | SAIDI=total G/total customers
|  | 3.3137 | CAIDI=SAIDI/SAIFI
|  | 0.99949 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00051304 | ASUI=1-ASAI
|  | 12054.5156 | ENS=total ENS*1000
|  | 11.1616 | AENS=ENS/total customers

## F3_(11-15)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3419.6969
0.1 | 0.075 | 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | B | 23514.0812
0.1 | 0.075 |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | C | 5325.4937
0.1 | 0.075 |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 5756.3156
0.1 | 0.075 |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | E | 3419.6969
0.1 | 0.075 |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | F | 12679.3156
0.1 | 0.075 |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
0.1 | 0.075 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | Calculation |  |  | 0.42625 |  | 1.3131 | 3.0806 | 0.545 | 0.71565 | 93.775 | 288.8875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.3019 | 3.0814 | 0.545 | 0.70952 | 92.95 | 286.4125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.3019 | 3.0814 | 0.545 | 0.70952 | 92.95 | 286.4125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4675 |  | 1.2681 | 2.7126 | 0.5 | 0.63406 | 93.5 | 253.625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4675 |  | 1.3019 | 2.7848 | 0.5 | 0.65094 | 93.5 | 260.375
[11 empty] | Total | 3.4197 | 466.675 | 1375.7125
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 466.675 | total F
|  | 0.44026 | SAIFI=total F/total customers
|  | 1.2978 | SAIDI=total G/total customers
|  | 2.9479 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014816 | ASUI=1-ASAI
|  | 3419.6969 | ENS=total ENS*1000
|  | 3.2261 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.545 | 4.8634 | 295.075 | 1963.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.545 | 4.8634 | 295.075 | 1963.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.545 | 4.8634 | 295.075 | 1963.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.5 | 4.4619 | 268.25 | 1784.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.5 | 4.4619 | 268.25 | 1784.75
[11 empty] | Total | 23.5141 | 1421.725 | 9459.175
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1421.725 | total F
|  | 1.3413 | SAIFI=total F/total customers
|  | 8.9238 | SAIDI=total G/total customers
|  | 6.6533 | CAIDI=SAIDI/SAIFI
|  | 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0010187 | ASUI=1-ASAI
|  | 23514.0812 | ENS=total ENS*1000
|  | 22.1831 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.42625 |  | 1.9788 | 4.6422 | 0.545 | 1.0784 | 93.775 | 435.325
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.9675 | 4.6568 | 0.545 | 1.0723 | 92.95 | 432.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.9675 | 4.6568 | 0.545 | 1.0723 | 92.95 | 432.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4675 |  | 2.1025 | 4.4973 | 0.5 | 1.0513 | 93.5 | 420.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4675 |  | 2.1025 | 4.4973 | 0.5 | 1.0513 | 93.5 | 420.5
[11 empty] | Total | 5.3255 | 466.675 | 2142.025
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 466.675 | total F
|  | 0.44026 | SAIFI=total F/total customers
|  | 2.0208 | SAIDI=total G/total customers
|  | 4.59 | CAIDI=SAIDI/SAIFI
|  | 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00023068 | ASUI=1-ASAI
|  | 5325.4937 | ENS=total ENS*1000
|  | 5.0241 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 1.7706 | 1.3201 | 0.545 | 0.96499 | 295.075 | 389.5375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 1.7613 | 1.3131 | 0.545 | 0.95988 | 295.075 | 387.475
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 2.8237 | 2.1053 | 0.545 | 1.5389 | 295.075 | 621.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 2.8237 | 2.1053 | 0.5 | 1.4119 | 268.25 | 564.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 1.7613 | 1.3131 | 0.5 | 0.88063 | 268.25 | 352.25
[11 empty] | Total | 5.7563 | 1421.725 | 2315.2375
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1421.725 | total F
|  | 1.3413 | SAIFI=total F/total customers
|  | 2.1842 | SAIDI=total G/total customers
|  | 1.6285 | CAIDI=SAIDI/SAIFI
|  | 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00024934 | ASUI=1-ASAI
|  | 5756.3156 | ENS=total ENS*1000
|  | 5.4305 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.42625 |  | 1.3131 | 3.0806 | 0.545 | 0.71565 | 93.775 | 288.8875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.3019 | 3.0814 | 0.545 | 0.70952 | 92.95 | 286.4125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4225 |  | 1.3019 | 3.0814 | 0.545 | 0.70952 | 92.95 | 286.4125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4675 |  | 1.2681 | 2.7126 | 0.5 | 0.63406 | 93.5 | 253.625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.4675 |  | 1.3019 | 2.7848 | 0.5 | 0.65094 | 93.5 | 260.375
[11 empty] | Total | 3.4197 | 466.675 | 1375.7125
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 466.675 | total F
|  | 0.44026 | SAIFI=total F/total customers
|  | 1.2978 | SAIDI=total G/total customers
|  | 2.9479 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014816 | ASUI=1-ASAI
|  | 3419.6969 | ENS=total ENS*1000
|  | 3.2261 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 1.9113 | 1.425 | 0.545 | 1.0416 | 295.075 | 420.475
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 3.1144 | 2.322 | 0.545 | 1.6973 | 295.075 | 685.1625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 5.4175 | 4.0391 | 0.545 | 2.9525 | 295.075 | 1191.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.3413 |  | 5.4175 | 4.0391 | 0.5 | 2.7087 | 268.25 | 1083.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.3413 |  | 8.5581 | 6.3807 | 0.5 | 4.2791 | 268.25 | 1711.625
[11 empty] | Total | 12.6793 | 1421.725 | 5092.6125
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1421.725 | total F
|  | 1.3413 | SAIFI=total F/total customers
|  | 4.8044 | SAIDI=total G/total customers
|  | 3.582 | CAIDI=SAIDI/SAIFI
|  | 0.99945 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00054844 | ASUI=1-ASAI
|  | 12679.3156 | ENS=total ENS*1000
|  | 11.9616 | AENS=ENS/total customers

## F4_(18-23)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 4134.5063
0.1 | 0.075 | 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | B | 32129.925
0.1 | 0.075 |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 6400.2562
0.1 | 0.075 |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 8123.6125
0.1 | 0.075 |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | E | 4134.5063
0.1 | 0.075 |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | F | 16579.55
0.1 | 0.075 |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
0.1 | 0.075 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
| 0.075 |  |  | x former |  |  | 0 | 0 | 0
| 0.075 |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.545 | 0.69624 | 94.6 | 281.05
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.5 | 0.63875 | 86 | 255.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.5 | 0.65563 | 88.25 | 262.25
[11 empty] | Total | 4.1345 | 560.075 | 1664.225
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 560.075 | total F
|  | 0.43756 | SAIFI=total F/total customers
|  | 1.3002 | SAIDI=total G/total customers
|  | 2.9714 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014842 | ASUI=1-ASAI
|  | 4134.5063 | ENS=total ENS*1000
|  | 3.2301 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.545 | 5.5065 | 330.275 | 2222.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.545 | 5.5065 | 330.275 | 2222.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.545 | 5.5065 | 330.275 | 2222.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.545 | 5.5065 | 330.275 | 2222.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.5 | 5.0519 | 300.25 | 2020.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.5 | 5.0519 | 300.25 | 2020.75
[11 empty] | Total | 32.1299 | 1921.6 | 12932.8
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1921.6 | total F
|  | 1.5013 | SAIFI=total F/total customers
|  | 10.1037 | SAIDI=total G/total customers
|  | 6.7302 | CAIDI=SAIDI/SAIFI
|  | 0.99885 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0011534 | ASUI=1-ASAI
|  | 32129.925 | ENS=total ENS*1000
|  | 25.1015 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.545 | 1.1029 | 97.075 | 445.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.545 | 1.0846 | 94.6 | 437.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.545 | 1.1029 | 97.075 | 445.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.545 | 1.1029 | 97.075 | 445.225
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.5 | 0.995 | 86 | 398
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.5 | 1.0119 | 88.25 | 404.75
[11 empty] | Total | 6.4003 | 560.075 | 2576.225
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 560.075 | total F
|  | 0.43756 | SAIFI=total F/total customers
|  | 2.0127 | SAIDI=total G/total customers
|  | 4.5998 | CAIDI=SAIDI/SAIFI
|  | 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00022976 | ASUI=1-ASAI
|  | 6400.2562 | ENS=total ENS*1000
|  | 5.0002 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 1.8413 | 1.2265 | 0.545 | 1.0035 | 330.275 | 405.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.545 | 1.5825 | 330.275 | 638.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.545 | 1.5825 | 330.275 | 638.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.545 | 1.5825 | 330.275 | 638.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.5 | 1.4519 | 300.25 | 580.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 1.8413 | 1.2265 | 0.5 | 0.92063 | 300.25 | 368.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
[11 empty] | Total | 8.1236 | 1921.6 | 3270.55
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1921.6 | total F
|  | 1.5013 | SAIFI=total F/total customers
|  | 2.5551 | SAIDI=total G/total customers
|  | 1.702 | CAIDI=SAIDI/SAIFI
|  | 0.99971 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00029168 | ASUI=1-ASAI
|  | 8123.6125 | ENS=total ENS*1000
|  | 6.3466 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.545 | 0.69624 | 94.6 | 281.05
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.5 | 0.63875 | 86 | 255.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.5 | 0.65563 | 88.25 | 262.25
[11 empty] | Total | 4.1345 | 560.075 | 1664.225
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 560.075 | total F
|  | 0.43756 | SAIFI=total F/total customers
|  | 1.3002 | SAIDI=total G/total customers
|  | 2.9714 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014842 | ASUI=1-ASAI
|  | 4134.5063 | ENS=total ENS*1000
|  | 3.2301 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 1.9913 | 1.3264 | 0.545 | 1.0852 | 330.275 | 438.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 4.2944 | 2.8605 | 0.545 | 2.3404 | 330.275 | 944.7625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 4.2944 | 2.8605 | 0.545 | 2.3404 | 330.275 | 944.7625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 6.5975 | 4.3947 | 0.545 | 3.5956 | 330.275 | 1451.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 6.5975 | 4.3947 | 0.5 | 3.2987 | 300.25 | 1319.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.5013 |  | 7.8381 | 5.2211 | 0.5 | 3.9191 | 300.25 | 1567.625
[11 empty] | Total | 16.5796 | 1921.6 | 6666.175
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1921.6 | total F
|  | 1.5013 | SAIFI=total F/total customers
|  | 5.2079 | SAIDI=total G/total customers
|  | 3.4691 | CAIDI=SAIDI/SAIFI
|  | 0.99941 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00059451 | ASUI=1-ASAI
|  | 16579.55 | ENS=total ENS*1000
|  | 12.9528 | AENS=ENS/total customers

## F7_(32-37)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 4134.675
0.1 | 0.075 | 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | B | 28413.3
0.1 | 0.075 |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | C | 6512.25
0.1 | 0.075 |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | D | 7307.175
0.1 | 0.075 |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | E | 4134.675
0.1 | 0.075 |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | F | 16446.8937
0.1 | 0.075 |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
0.1 | 0.075 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.075 |  |  | Calculation |  |  | 0.43 |  | 1.315 | 3.0581 | 0.545 | 0.71668 | 94.6 | 289.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.315 | 3.0581 | 0.545 | 0.71668 | 94.6 | 289.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.415 |  | 1.27 | 3.0602 | 0.545 | 0.69215 | 91.3 | 279.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 1.315 | 2.7684 | 0.545 | 0.71668 | 104.5 | 289.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 1.27 | 2.6737 | 0.5 | 0.635 | 95 | 254
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 1.315 | 2.7684 | 0.5 | 0.6575 | 95 | 263
[11 empty] | Total | 4.1347 | 575 | 1664.3
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 575 | total F
|  | 0.44922 | SAIFI=total F/total customers
|  | 1.3002 | SAIDI=total G/total customers
|  | 2.8944 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014843 | ASUI=1-ASAI
|  | 4134.675 | ENS=total ENS*1000
|  | 3.2302 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.545 | 4.8696 | 295.9 | 1965.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.545 | 4.8696 | 295.9 | 1965.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.545 | 4.8696 | 295.9 | 1965.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.545 | 4.8696 | 295.9 | 1965.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.5 | 4.4675 | 269 | 1787
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.5 | 4.4675 | 269 | 1787
[11 empty] | Total | 28.4133 | 1721.6 | 11436.8
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1721.6 | total F
|  | 1.345 | SAIFI=total F/total customers
|  | 8.935 | SAIDI=total G/total customers
|  | 6.6431 | CAIDI=SAIDI/SAIFI
|  | 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00102 | ASUI=1-ASAI
|  | 28413.3 | ENS=total ENS*1000
|  | 22.1979 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.545 | 1.0845 | 94.6 | 437.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.545 | 1.0845 | 94.6 | 437.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.415 |  | 1.945 | 4.6867 | 0.545 | 1.06 | 91.3 | 427.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 2.125 | 4.4737 | 0.545 | 1.1581 | 104.5 | 467.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 2.125 | 4.4737 | 0.5 | 1.0625 | 95 | 425
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 2.125 | 4.4737 | 0.5 | 1.0625 | 95 | 425
[11 empty] | Total | 6.5122 | 575 | 2621
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 575 | total F
|  | 0.44922 | SAIFI=total F/total customers
|  | 2.0477 | SAIDI=total G/total customers
|  | 4.5583 | CAIDI=SAIDI/SAIFI
|  | 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00023375 | ASUI=1-ASAI
|  | 6512.25 | ENS=total ENS*1000
|  | 5.0877 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 1.7725 | 1.3178 | 0.545 | 0.96601 | 295.9 | 389.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 1.7725 | 1.3178 | 0.545 | 0.96601 | 295.9 | 389.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 2.835 | 2.1078 | 0.545 | 1.5451 | 295.9 | 623.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 2.835 | 2.1078 | 0.545 | 1.5451 | 295.9 | 623.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 1.735 | 1.29 | 0.5 | 0.8675 | 269 | 347
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 2.835 | 2.1078 | 0.5 | 1.4175 | 269 | 567
[11 empty] | Total | 7.3072 | 1721.6 | 2941.3
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1721.6 | total F
|  | 1.345 | SAIFI=total F/total customers
|  | 2.2979 | SAIDI=total G/total customers
|  | 1.7085 | CAIDI=SAIDI/SAIFI
|  | 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026232 | ASUI=1-ASAI
|  | 7307.175 | ENS=total ENS*1000
|  | 5.7087 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.315 | 3.0581 | 0.545 | 0.71668 | 94.6 | 289.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.43 |  | 1.315 | 3.0581 | 0.545 | 0.71668 | 94.6 | 289.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.415 |  | 1.27 | 3.0602 | 0.545 | 0.69215 | 91.3 | 279.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 1.315 | 2.7684 | 0.545 | 0.71668 | 104.5 | 289.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 1.27 | 2.6737 | 0.5 | 0.635 | 95 | 254
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.475 |  | 1.315 | 2.7684 | 0.5 | 0.6575 | 95 | 263
[11 empty] | Total | 4.1347 | 575 | 1664.3
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 575 | total F
|  | 0.44922 | SAIFI=total F/total customers
|  | 1.3002 | SAIDI=total G/total customers
|  | 2.8944 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014843 | ASUI=1-ASAI
|  | 4134.675 | ENS=total ENS*1000
|  | 3.2302 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 1.9131 | 1.4224 | 0.545 | 1.0427 | 295.9 | 420.8875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 3.1256 | 2.3239 | 0.545 | 1.7035 | 295.9 | 687.6375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 5.4287 | 4.0362 | 0.545 | 2.9587 | 295.9 | 1194.325
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 5.4287 | 4.0362 | 0.545 | 2.9587 | 295.9 | 1194.325
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.345 |  | 6.6319 | 4.9308 | 0.5 | 3.3159 | 269 | 1326.375
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.5 | 4.4675 | 269 | 1787
[11 empty] | Total | 16.4469 | 1721.6 | 6610.55
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1721.6 | total F
|  | 1.345 | SAIFI=total F/total customers
|  | 5.1645 | SAIDI=total G/total customers
|  | 3.8398 | CAIDI=SAIDI/SAIFI
|  | 0.99941 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00058955 | ASUI=1-ASAI
|  | 16446.8937 | ENS=total ENS*1000
|  | 12.8491 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 3473.4438 |  | 24036.25 |  | 5332.6938 |  | 5859.0938 |  | 3473.4438 |  | 12054.516
Feeder 3 | 3419.6969 |  | 23514.0813 |  | 5325.4937 |  | 5756.3156 |  | 3419.6969 |  | 12679.3156
Feeder 4 | 4134.506 |  | 32129.93 |  | 6400.256 |  | 8123.613 |  | 4134.506 |  | 16579.55
Feeder 7 | 4134.675 |  | 28413.3 |  | 6512.25 |  | 7307.175 |  | 4134.675 |  | 16446.89
TOTAL | 15162.3217 |  | 108093.5613 |  | 23570.6935 |  | 27046.1974 |  | 15162.3217 |  | 57760.2716
Analytic | 15.1623 |  | 108.0936 |  | 23.5707 |  | 27.0462 |  | 15.1623 |  | 57.7603
Monte Carlo_Code | 15.16 |  | 108.0692 |  | 23.1919 |  | 27.0421 |  | 15.162 |  | 56.9021
Deviation | 0.015312 |  | 0.022537 |  | 1.6071 |  | 0.01515 |  | 0.0021216 |  | 1.4857
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 15.16 | 15.1942 | 15.1736 | 15.1797 |  | 945000 | 108.0947 | 108.075 | 108.0692 | 108.0879
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 23.2107 | 23.2115 | 23.1919 | 23.1692 |  | 47500 | 27.0822 | 27.0624 | 27.0421 | 27.0883
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 15.162 | 15.1776 | 15.2202 | 15.1926 |  | 1140000 | 56.7771 | 56.8835 | 56.9021 | 56.8644