## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 856.875
0.075 | 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | B | 3425.625
0.075 |  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 2300.625
0.075 |  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | D | 1044.375
0.075 |  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135 | [5 empty] | E | 856.875
0.075 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 2478.75
0.075 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | Calculation |  |  | 0.21 |  | 0.2175 | 1.0357 | 1 | 0.2175 | 0.21 | 0.2175
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.25125 | 1.1356 | 1.5 | 0.37687 | 0.22125 | 0.25125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.225 |  | 0.2625 | 1.1667 | 1 | 0.2625 | 0.225 | 0.2625
[10 empty] | Total | 0.85687 | 0.65625 | 0.73125
| 3 | total customers
| 26280 | total (customers*8760)
| 0.65625 | total F
| 0.21875 | SAIFI=total F/total customers
| 0.24375 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.7825e-05 | ASUI=1-ASAI
| 856.875 | ENS=total ENS*1000
| 285.625 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.97875 | 3 | 1 | 0.97875 | 0.32625 | 0.97875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.97875 | 3 | 1.5 | 1.4681 | 0.32625 | 0.97875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.97875 | 3 | 1 | 0.97875 | 0.32625 | 0.97875
[10 empty] | Total | 3.4256 | 0.97875 | 2.9363
| 3 | total customers
| 26280 | total (customers*8760)
| 0.97875 | total F
| 0.32625 | SAIFI=total F/total customers
| 0.97875 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00011173 | ASUI=1-ASAI
| 3425.625 | ENS=total ENS*1000
| 1141.875 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.21 |  | 0.63 | 3 | 1 | 0.63 | 0.21 | 0.63
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.66375 | 3 | 1.5 | 0.99562 | 0.22125 | 0.66375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.225 |  | 0.675 | 3 | 1 | 0.675 | 0.225 | 0.675
[10 empty] | Total | 2.3006 | 0.65625 | 1.9688
| 3 | total customers
| 26280 | total (customers*8760)
| 0.65625 | total F
| 0.21875 | SAIFI=total F/total customers
| 0.65625 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.4914e-05 | ASUI=1-ASAI
| 2300.625 | ENS=total ENS*1000
| 766.875 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 18 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.32625 |  | 0.27563 | 0.84483 | 1 | 0.27563 | 0.32625 | 0.27563
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.32625 |  | 0.30375 | 0.93103 | 1.5 | 0.45562 | 0.32625 | 0.30375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.31312 | 0.95977 | 1 | 0.31312 | 0.32625 | 0.31312
[10 empty] | Total | 1.0444 | 0.97875 | 0.8925
| 3 | total customers
| 26280 | total (customers*8760)
| 0.97875 | total F
| 0.32625 | SAIFI=total F/total customers
| 0.2975 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.3961e-05 | ASUI=1-ASAI
| 1044.375 | ENS=total ENS*1000
| 348.125 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 18 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.32625 |  | 0.42563 | 1.3046 | 1 | 0.42563 | 0.32625 | 0.42563
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.32625 |  | 0.71625 | 2.1954 | 1.5 | 1.0744 | 0.32625 | 0.71625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.97875 | 3 | 1 | 0.97875 | 0.32625 | 0.97875
[10 empty] | Total | 2.4787 | 0.97875 | 2.1206
| 3 | total customers
| 26280 | total (customers*8760)
| 0.97875 | total F
| 0.32625 | SAIFI=total F/total customers
| 0.70688 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 8.0693e-05 | ASUI=1-ASAI
| 2478.75 | ENS=total ENS*1000
| 826.25 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 725.625
0.075 | 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | B | 2902.5
0.075 |  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225 | [5 empty] | C | 1935
0.075 |  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | D | 886.875
0.075 |  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875 | [5 empty] | E | 725.625
0.075 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 2133.75
0.075 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | Calculation |  |  | 0.2175 |  | 0.24937 | 1.1466 | 1 | 0.24937 | 0.2175 | 0.24937
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.26062 | 1.178 | 1 | 0.26062 | 0.22125 | 0.26062
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.20625 |  | 0.21563 | 1.0455 | 1 | 0.21563 | 0.20625 | 0.21563
[10 empty] | Total | 0.72562 | 0.645 | 0.72562
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.24187 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.7611e-05 | ASUI=1-ASAI
| 725.625 | ENS=total ENS*1000
| 241.875 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
[10 empty] | Total | 2.9025 | 0.9675 | 2.9025
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.9675 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00011045 | ASUI=1-ASAI
| 2902.5 | ENS=total ENS*1000
| 967.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1 | 0.6525 | 0.2175 | 0.6525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.66375 | 3 | 1 | 0.66375 | 0.22125 | 0.66375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.20625 |  | 0.61875 | 3 | 1 | 0.61875 | 0.20625 | 0.61875
[10 empty] | Total | 1.935 | 0.645 | 1.935
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.645 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.363e-05 | ASUI=1-ASAI
| 1935 | ENS=total ENS*1000
| 645 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 49 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.30188 | 0.93605 | 1 | 0.30188 | 0.3225 | 0.30188
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.31125 | 0.96512 | 1 | 0.31125 | 0.3225 | 0.31125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 47 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.27375 | 0.84884 | 1 | 0.27375 | 0.3225 | 0.27375
[10 empty] | Total | 0.88688 | 0.9675 | 0.88688
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.29563 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.3747e-05 | ASUI=1-ASAI
| 886.875 | ENS=total ENS*1000
| 295.625 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 49 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.45187 | 1.4012 | 1 | 0.45187 | 0.3225 | 0.45187
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.71437 | 2.2151 | 1 | 0.71437 | 0.3225 | 0.71437
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
[10 empty] | Total | 2.1338 | 0.9675 | 2.1338
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.71125 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 8.1193e-05 | ASUI=1-ASAI
| 2133.75 | ENS=total ENS*1000
| 711.25 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 814.6875
0.075 | 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125 | [5 empty] | B | 3386.25
0.075 |  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 2356.875
0.075 |  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 986.25
0.075 |  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135 | [5 empty] | E | 814.6875
0.075 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 2570.625
0.075 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | Calculation |  |  | 0.22125 |  | 0.22313 | 1.0085 | 1 | 0.22313 | 0.22125 | 0.22313
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.2325 |  | 0.25687 | 1.1048 | 1 | 0.25687 | 0.2325 | 0.25687
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.22125 |  | 0.22313 | 1.0085 | 1.5 | 0.33469 | 0.22125 | 0.22313
[10 empty] | Total | 0.81469 | 0.675 | 0.70312
| 3 | total customers
| 26280 | total (customers*8760)
| 0.675 | total F
| 0.225 | SAIFI=total F/total customers
| 0.23438 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.6755e-05 | ASUI=1-ASAI
| 814.6875 | ENS=total ENS*1000
| 271.5625 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1.5 | 1.4512 | 0.3225 | 0.9675
[10 empty] | Total | 3.3862 | 0.9675 | 2.9025
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.9675 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00011045 | ASUI=1-ASAI
| 3386.25 | ENS=total ENS*1000
| 1128.75 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.66375 | 3 | 1 | 0.66375 | 0.22125 | 0.66375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.2325 |  | 0.6975 | 3 | 1 | 0.6975 | 0.2325 | 0.6975
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.22125 |  | 0.66375 | 3 | 1.5 | 0.99563 | 0.22125 | 0.66375
[10 empty] | Total | 2.3569 | 0.675 | 2.025
| 3 | total customers
| 26280 | total (customers*8760)
| 0.675 | total F
| 0.225 | SAIFI=total F/total customers
| 0.675 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.7055e-05 | ASUI=1-ASAI
| 2356.875 | ENS=total ENS*1000
| 785.625 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 55 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.27375 | 0.84884 | 1 | 0.27375 | 0.3225 | 0.27375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.30188 | 0.93605 | 1 | 0.30188 | 0.3225 | 0.30188
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.27375 | 0.84884 | 1.5 | 0.41063 | 0.3225 | 0.27375
[10 empty] | Total | 0.98625 | 0.9675 | 0.84937
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.28313 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.232e-05 | ASUI=1-ASAI
| 986.25 | ENS=total ENS*1000
| 328.75 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 55 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.41438 | 1.2849 | 1 | 0.41438 | 0.3225 | 0.41438
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.705 | 2.186 | 1 | 0.705 | 0.3225 | 0.705
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1.5 | 1.4512 | 0.3225 | 0.9675
[10 empty] | Total | 2.5706 | 0.9675 | 2.0869
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.69563 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.9409e-05 | ASUI=1-ASAI
| 2570.625 | ENS=total ENS*1000
| 856.875 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 2 | 856.88 |  | 3425.6 |  | 2300.6 |  | 1044.4 |  | 856.88 |  | 2478.8
Feeder 5 | 725.625 |  | 2902.5 |  | 1935 |  | 886.875 |  | 725.625 |  | 2133.75
Feeder 6 | 814.6875 |  | 3386.25 |  | 2356.875 |  | 986.25 |  | 814.6875 |  | 2570.625
TOTAL | 2397.1925 |  | 9714.35 |  | 6592.475 |  | 2917.525 |  | 2397.1925 |  | 7183.175
Analytic | 2.3972 |  | 9.7143 |  | 6.5925 |  | 2.9175 |  | 2.3972 |  | 7.1832
Monte Carlo_Code | 2.3885 |  | 9.6238 |  | 6.5874 |  | 2.9158 |  | 2.3945 |  | 7.1571
Deviation | 0.36261 |  | 0.93213 |  | 0.076982 |  | 0.059125 |  | 0.11232 |  | 0.363
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 2.3993 | 2.4011 | 2.3976 | 2.3885 |  | 945000 | 9.6238 | 9.7129 | 9.6827 | 9.7349
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 6.5874 | 6.6039 | 6.6258 | 6.6003 |  | 47500 | 2.9158 | 2.9349 | 2.9155 | 2.9188
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 2.4012 | 2.3945 | 2.3486 | 2.3993 |  | 1140000 | 7.1954 | 7.1969 | 7.1571 | 7.1935