## F1_(6-7)
[7 empty] | CASE A | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1176.525
0.1 | 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 7988.75
0.1 |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 1944.275
0.1 |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 2552.25
0.1 |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | E | 1176.525
0.1 |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 7988.75
0.1 |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
0.1 |  |  | 12 | 0.75 | 0.1 | 0.075 | 0 | 0
0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.425 | 2.28 | 0.415 | 0.59137 | 6.25 | 14.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.41 | 2.256 | 0.415 | 0.58515 | 6.25 | 14.1
[10 empty] | Total | 1.1765 | 12.5 | 28.35
| 20 | total customers
| 175200 | total (customers*8760)
| 12.5 | total F
| 0.625 | SAIFI=total F/total customers
| 1.4175 | SAIDI=total G/total customers
| 2.268 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016182 | ASUI=1-ASAI
| 1176.525 | ENS=total ENS*1000
| 58.8263 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.415 | 3.9944 | 15.75 | 96.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.415 | 3.9944 | 15.75 | 96.25
[10 empty] | Total | 7.9887 | 31.5 | 192.5
| 20 | total customers
| 175200 | total (customers*8760)
| 31.5 | total F
| 1.575 | SAIFI=total F/total customers
| 9.625 | SAIDI=total G/total customers
| 6.1111 | CAIDI=SAIDI/SAIFI
| 0.9989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010987 | ASUI=1-ASAI
| 7988.75 | ENS=total ENS*1000
| 399.4375 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 2.35 | 3.76 | 0.415 | 0.97525 | 6.25 | 23.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 2.335 | 3.736 | 0.415 | 0.96902 | 6.25 | 23.35
[10 empty] | Total | 1.9443 | 12.5 | 46.85
| 20 | total customers
| 175200 | total (customers*8760)
| 12.5 | total F
| 0.625 | SAIFI=total F/total customers
| 2.3425 | SAIDI=total G/total customers
| 3.748 | CAIDI=SAIDI/SAIFI
| 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00026741 | ASUI=1-ASAI
| 1944.275 | ENS=total ENS*1000
| 97.2137 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 3.075 | 1.9524 | 0.415 | 1.2761 | 15.75 | 30.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 3.075 | 1.9524 | 0.415 | 1.2761 | 15.75 | 30.75
[10 empty] | Total | 2.5522 | 31.5 | 61.5
| 20 | total customers
| 175200 | total (customers*8760)
| 31.5 | total F
| 1.575 | SAIFI=total F/total customers
| 3.075 | SAIDI=total G/total customers
| 1.9524 | CAIDI=SAIDI/SAIFI
| 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00035103 | ASUI=1-ASAI
| 2552.25 | ENS=total ENS*1000
| 127.6125 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.425 | 2.28 | 0.415 | 0.59137 | 6.25 | 14.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.41 | 2.256 | 0.415 | 0.58515 | 6.25 | 14.1
[10 empty] | Total | 1.1765 | 12.5 | 28.35
| 20 | total customers
| 175200 | total (customers*8760)
| 12.5 | total F
| 0.625 | SAIFI=total F/total customers
| 1.4175 | SAIDI=total G/total customers
| 2.268 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016182 | ASUI=1-ASAI
| 1176.525 | ENS=total ENS*1000
| 58.8263 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.415 | 3.9944 | 15.75 | 96.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.415 | 3.9944 | 15.75 | 96.25
[10 empty] | Total | 7.9887 | 31.5 | 192.5
| 20 | total customers
| 175200 | total (customers*8760)
| 31.5 | total F
| 1.575 | SAIFI=total F/total customers
| 9.625 | SAIDI=total G/total customers
| 6.1111 | CAIDI=SAIDI/SAIFI
| 0.9989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010987 | ASUI=1-ASAI
| 7988.75 | ENS=total ENS*1000
| 399.4375 | AENS=ENS/total customers

## F3_(16-17)
[7 empty] | CASE A | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1145.4
0.1 | 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 7938.95
0.1 |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 2050.1
0.1 |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 2502.45
0.1 |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | E | 1145.4
0.1 |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 7938.95
0.1 |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
0.1 |  |  | 30 | 0.6 | 0.1 | 0.06 | 0 | 0
0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.4025 | 2.3771 | 0.415 | 0.58204 | 5.9 | 14.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.3575 | 2.3008 | 0.415 | 0.56336 | 5.9 | 13.575
[10 empty] | Total | 1.1454 | 11.8 | 27.6
| 20 | total customers
| 175200 | total (customers*8760)
| 11.8 | total F
| 0.59 | SAIFI=total F/total customers
| 1.38 | SAIDI=total G/total customers
| 2.339 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015753 | ASUI=1-ASAI
| 1145.4 | ENS=total ENS*1000
| 57.27 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.415 | 3.9695 | 15.55 | 95.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.415 | 3.9695 | 15.55 | 95.65
[10 empty] | Total | 7.939 | 31.1 | 191.3
| 20 | total customers
| 175200 | total (customers*8760)
| 31.1 | total F
| 1.555 | SAIFI=total F/total customers
| 9.565 | SAIDI=total G/total customers
| 6.1511 | CAIDI=SAIDI/SAIFI
| 0.99891 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010919 | ASUI=1-ASAI
| 7938.95 | ENS=total ENS*1000
| 396.9475 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 2.47 | 4.1864 | 0.415 | 1.025 | 5.9 | 24.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 2.47 | 4.1864 | 0.415 | 1.025 | 5.9 | 24.7
[10 empty] | Total | 2.0501 | 11.8 | 49.4
| 20 | total customers
| 175200 | total (customers*8760)
| 11.8 | total F
| 0.59 | SAIFI=total F/total customers
| 2.47 | SAIDI=total G/total customers
| 4.1864 | CAIDI=SAIDI/SAIFI
| 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00028196 | ASUI=1-ASAI
| 2050.1 | ENS=total ENS*1000
| 102.505 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 3.015 | 1.9389 | 0.415 | 1.2512 | 15.55 | 30.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 3.015 | 1.9389 | 0.415 | 1.2512 | 15.55 | 30.15
[10 empty] | Total | 2.5024 | 31.1 | 60.3
| 20 | total customers
| 175200 | total (customers*8760)
| 31.1 | total F
| 1.555 | SAIFI=total F/total customers
| 3.015 | SAIDI=total G/total customers
| 1.9389 | CAIDI=SAIDI/SAIFI
| 0.99966 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00034418 | ASUI=1-ASAI
| 2502.45 | ENS=total ENS*1000
| 125.1225 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.4025 | 2.3771 | 0.415 | 0.58204 | 5.9 | 14.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.3575 | 2.3008 | 0.415 | 0.56336 | 5.9 | 13.575
[10 empty] | Total | 1.1454 | 11.8 | 27.6
| 20 | total customers
| 175200 | total (customers*8760)
| 11.8 | total F
| 0.59 | SAIFI=total F/total customers
| 1.38 | SAIDI=total G/total customers
| 2.339 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015753 | ASUI=1-ASAI
| 1145.4 | ENS=total ENS*1000
| 57.27 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.415 | 3.9695 | 15.55 | 95.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.415 | 3.9695 | 15.55 | 95.65
[10 empty] | Total | 7.939 | 31.1 | 191.3
| 20 | total customers
| 175200 | total (customers*8760)
| 31.1 | total F
| 1.555 | SAIFI=total F/total customers
| 9.565 | SAIDI=total G/total customers
| 6.1511 | CAIDI=SAIDI/SAIFI
| 0.99891 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010919 | ASUI=1-ASAI
| 7938.95 | ENS=total ENS*1000
| 396.9475 | AENS=ENS/total customers

## F4_(24-25)
[7 empty] | CASE A | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1155.775
0.1 | 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | B | 8968.15
0.1 |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 1944.275
0.1 |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 2577.15
0.1 |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | E | 1155.775
0.1 |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 8968.15
0.1 |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
0.1 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
0.1 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.415 | 0.58722 | 5.55 | 14.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.415 | 0.56855 | 5.4 | 13.7
[10 empty] | Total | 1.1558 | 10.95 | 27.85
| 20 | total customers
| 175200 | total (customers*8760)
| 10.95 | total F
| 0.5475 | SAIFI=total F/total customers
| 1.3925 | SAIDI=total G/total customers
| 2.5434 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015896 | ASUI=1-ASAI
| 1155.775 | ENS=total ENS*1000
| 57.7888 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.415 | 4.4841 | 17.35 | 108.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.415 | 4.4841 | 17.35 | 108.05
[10 empty] | Total | 8.9681 | 34.7 | 216.1
| 20 | total customers
| 175200 | total (customers*8760)
| 34.7 | total F
| 1.735 | SAIFI=total F/total customers
| 10.805 | SAIDI=total G/total customers
| 6.2277 | CAIDI=SAIDI/SAIFI
| 0.99877 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012334 | ASUI=1-ASAI
| 8968.15 | ENS=total ENS*1000
| 448.4075 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.415 | 0.98147 | 5.55 | 23.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.415 | 0.9628 | 5.4 | 23.2
[10 empty] | Total | 1.9443 | 10.95 | 46.85
| 20 | total customers
| 175200 | total (customers*8760)
| 10.95 | total F
| 0.5475 | SAIFI=total F/total customers
| 2.3425 | SAIDI=total G/total customers
| 4.2785 | CAIDI=SAIDI/SAIFI
| 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00026741 | ASUI=1-ASAI
| 1944.275 | ENS=total ENS*1000
| 97.2138 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.415 | 1.2886 | 17.35 | 31.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.415 | 1.2886 | 17.35 | 31.05
[10 empty] | Total | 2.5771 | 34.7 | 62.1
| 20 | total customers
| 175200 | total (customers*8760)
| 34.7 | total F
| 1.735 | SAIFI=total F/total customers
| 3.105 | SAIDI=total G/total customers
| 1.7896 | CAIDI=SAIDI/SAIFI
| 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00035445 | ASUI=1-ASAI
| 2577.15 | ENS=total ENS*1000
| 128.8575 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.415 | 0.58722 | 5.55 | 14.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.415 | 0.56855 | 5.4 | 13.7
[10 empty] | Total | 1.1558 | 10.95 | 27.85
| 20 | total customers
| 175200 | total (customers*8760)
| 10.95 | total F
| 0.5475 | SAIFI=total F/total customers
| 1.3925 | SAIDI=total G/total customers
| 2.5434 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015896 | ASUI=1-ASAI
| 1155.775 | ENS=total ENS*1000
| 57.7888 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.415 | 4.4841 | 17.35 | 108.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.415 | 4.4841 | 17.35 | 108.05
[10 empty] | Total | 8.9681 | 34.7 | 216.1
| 20 | total customers
| 175200 | total (customers*8760)
| 34.7 | total F
| 1.735 | SAIFI=total F/total customers
| 10.805 | SAIDI=total G/total customers
| 6.2277 | CAIDI=SAIDI/SAIFI
| 0.99877 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012334 | ASUI=1-ASAI
| 8968.15 | ENS=total ENS*1000
| 448.4075 | AENS=ENS/total customers

## F7_(38)
[7 empty] | CASE A | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 564.4
0.1 | 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 3975.7
0.1 |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 1037.5
0.1 |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | D | 1257.45
0.1 |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | E | 564.4
0.1 |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | F | 3975.7
0.1 |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 66 | 0.8 | 0.1 | 0.08 | 0 | 0
0.1 |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.36 | 2.2667 | 0.415 | 0.5644 | 6 | 13.6
[10 empty] | Total | 0.5644 | 6 | 13.6
| 10 | total customers
| 87600 | total (customers*8760)
| 6 | total F
| 0.6 | SAIFI=total F/total customers
| 1.36 | SAIDI=total G/total customers
| 2.2667 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015525 | ASUI=1-ASAI
| 564.4 | ENS=total ENS*1000
| 56.44 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.415 | 3.9757 | 15.6 | 95.8
[10 empty] | Total | 3.9757 | 15.6 | 95.8
| 10 | total customers
| 87600 | total (customers*8760)
| 15.6 | total F
| 1.56 | SAIFI=total F/total customers
| 9.58 | SAIDI=total G/total customers
| 6.141 | CAIDI=SAIDI/SAIFI
| 0.99891 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010936 | ASUI=1-ASAI
| 3975.7 | ENS=total ENS*1000
| 397.57 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 2.5 | 4.1667 | 0.415 | 1.0375 | 6 | 25
[10 empty] | Total | 1.0375 | 6 | 25
| 10 | total customers
| 87600 | total (customers*8760)
| 6 | total F
| 0.6 | SAIFI=total F/total customers
| 2.5 | SAIDI=total G/total customers
| 4.1667 | CAIDI=SAIDI/SAIFI
| 0.99971 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00028539 | ASUI=1-ASAI
| 1037.5 | ENS=total ENS*1000
| 103.75 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 3.03 | 1.9423 | 0.415 | 1.2574 | 15.6 | 30.3
[10 empty] | Total | 1.2574 | 15.6 | 30.3
| 10 | total customers
| 87600 | total (customers*8760)
| 15.6 | total F
| 1.56 | SAIFI=total F/total customers
| 3.03 | SAIDI=total G/total customers
| 1.9423 | CAIDI=SAIDI/SAIFI
| 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00034589 | ASUI=1-ASAI
| 1257.45 | ENS=total ENS*1000
| 125.745 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.36 | 2.2667 | 0.415 | 0.5644 | 6 | 13.6
[10 empty] | Total | 0.5644 | 6 | 13.6
| 10 | total customers
| 87600 | total (customers*8760)
| 6 | total F
| 0.6 | SAIFI=total F/total customers
| 1.36 | SAIDI=total G/total customers
| 2.2667 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015525 | ASUI=1-ASAI
| 564.4 | ENS=total ENS*1000
| 56.44 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.415 | 3.9757 | 15.6 | 95.8
[10 empty] | Total | 3.9757 | 15.6 | 95.8
| 10 | total customers
| 87600 | total (customers*8760)
| 15.6 | total F
| 1.56 | SAIFI=total F/total customers
| 9.58 | SAIDI=total G/total customers
| 6.141 | CAIDI=SAIDI/SAIFI
| 0.99891 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010936 | ASUI=1-ASAI
| 3975.7 | ENS=total ENS*1000
| 397.57 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 1176.525 | 20 | 7988.75 | 20 | 1944.275 | 20 | 2552.25 | 20 | 1176.525 | 20 | 7988.75 | 20
Feeder 3 | 1145.4 | 20 | 7938.95 | 20 | 2050.1 | 20 | 2502.45 | 20 | 1145.4 | 20 | 7938.95 | 20
Feeder 4 | 1155.775 | 20 | 8968.15 | 20 | 1944.275 | 20 | 2577.15 | 20 | 1155.775 | 20 | 8968.15 | 20
Feeder 7 | 564.4 | 10 | 3975.7 | 10 | 1037.5 | 10 | 1257.45 | 10 | 564.4 | 10 | 3975.7 | 10
TOTAL | 4042.1 | 70 | 28871.55 | 70 | 6976.15 | 70 | 8889.3 | 70 | 4042.1 | 70 | 28871.55 | 70
Analytic | 4.0421 |  | 28.8715 |  | 6.9761 |  | 8.8893 |  | 4.0421 |  | 28.8715
Monte Carlo_Code | 4.0413 |  | 28.8648 |  | 6.7238 |  | 8.8832 |  | 4.034 |  | 28.8647
Deviation | 0.019792 |  | 0.023379 |  | 3.6173 |  | 0.068622 |  | 0.20039 |  | 0.023726
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 4.0707 | 4.0413 | 4.0635 | 4.0469 |  | 945000 | 28.9076 | 28.9198 | 28.8603 | 28.8648
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 6.6993 | 6.7135 | 6.7238 | 6.7144 |  | 47500 | 8.9141 | 8.89 | 8.8846 | 8.8832
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 4.0459 | 4.034 | 4.0518 | 4.036 |  | 1140000 | 28.8647 | 28.8875 | 28.8768 | 28.8677