## F1_(1-5)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3737.925
0.1 | 0.1 | 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 25795
0.1 | 0.1 |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 6216.925
0.1 | 0.1 |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 6319.875
0.1 | 0.1 |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | E | 3737.925
0.1 | 0.1 |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 13069.9375
0.1 | 0.1 |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
0.1 | 0.1 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | Calculation |  |  | 0.53 |  | 1.365 | 2.5755 | 0.545 | 0.74393 | 116.6 | 300.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.545 |  | 1.41 | 2.5872 | 0.545 | 0.76845 | 119.9 | 310.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 1.365 | 2.5755 | 0.545 | 0.74393 | 116.6 | 300.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.625 |  | 1.425 | 2.28 | 0.545 | 0.77663 | 137.5 | 313.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.625 |  | 1.41 | 2.256 | 0.5 | 0.705 | 125 | 282
[11 empty] | Total | 3.7379 | 615.6 | 1506.3
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 615.6 | total F
|  | 0.57 | SAIFI=total F/total customers
|  | 1.3947 | SAIDI=total G/total customers
|  | 2.4469 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015921 | ASUI=1-ASAI
|  | 3737.925 | ENS=total ENS*1000
|  | 3.461 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.545 | 5.2456 | 346.5 | 2117.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.545 | 5.2456 | 346.5 | 2117.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.545 | 5.2456 | 346.5 | 2117.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.545 | 5.2456 | 346.5 | 2117.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.5 | 4.8125 | 315 | 1925
[11 empty] | Total | 25.795 | 1701 | 10395
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1701 | total F
|  | 1.575 | SAIFI=total F/total customers
|  | 9.625 | SAIDI=total G/total customers
|  | 6.1111 | CAIDI=SAIDI/SAIFI
|  | 0.9989 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0010987 | ASUI=1-ASAI
|  | 25795 | ENS=total ENS*1000
|  | 23.8843 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 2.29 | 4.3208 | 0.545 | 1.2481 | 116.6 | 503.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.545 |  | 2.335 | 4.2844 | 0.545 | 1.2726 | 119.9 | 513.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 2.29 | 4.3208 | 0.545 | 1.2481 | 116.6 | 503.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.625 |  | 2.35 | 3.76 | 0.545 | 1.2808 | 137.5 | 517
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.625 |  | 2.335 | 3.736 | 0.5 | 1.1675 | 125 | 467
[11 empty] | Total | 6.2169 | 615.6 | 2505.3
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 615.6 | total F
|  | 0.57 | SAIFI=total F/total customers
|  | 2.3197 | SAIDI=total G/total customers
|  | 4.0697 | CAIDI=SAIDI/SAIFI
|  | 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026481 | ASUI=1-ASAI
|  | 6216.925 | ENS=total ENS*1000
|  | 5.7564 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 1.8875 | 1.1984 | 0.545 | 1.0287 | 346.5 | 415.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 1.925 | 1.2222 | 0.545 | 1.0491 | 346.5 | 423.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 1.8875 | 1.1984 | 0.545 | 1.0287 | 346.5 | 415.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 3.075 | 1.9524 | 0.545 | 1.6759 | 346.5 | 676.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 3.075 | 1.9524 | 0.5 | 1.5375 | 315 | 615
[11 empty] | Total | 6.3199 | 1701 | 2545.5
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1701 | total F
|  | 1.575 | SAIFI=total F/total customers
|  | 2.3569 | SAIDI=total G/total customers
|  | 1.4965 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026906 | ASUI=1-ASAI
|  | 6319.875 | ENS=total ENS*1000
|  | 5.8517 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 1.365 | 2.5755 | 0.545 | 0.74393 | 116.6 | 300.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.545 |  | 1.41 | 2.5872 | 0.545 | 0.76845 | 119.9 | 310.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 1.365 | 2.5755 | 0.545 | 0.74393 | 116.6 | 300.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.625 |  | 1.425 | 2.28 | 0.545 | 0.77663 | 137.5 | 313.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.625 |  | 1.41 | 2.256 | 0.5 | 0.705 | 125 | 282
[11 empty] | Total | 3.7379 | 615.6 | 1506.3
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 615.6 | total F
|  | 0.57 | SAIFI=total F/total customers
|  | 1.3947 | SAIDI=total G/total customers
|  | 2.4469 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015921 | ASUI=1-ASAI
|  | 3737.925 | ENS=total ENS*1000
|  | 3.461 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 2.075 | 1.3175 | 0.545 | 1.1309 | 346.5 | 456.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 3.4125 | 2.1667 | 0.545 | 1.8598 | 346.5 | 750.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 4.7125 | 2.9921 | 0.545 | 2.5683 | 346.5 | 1036.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 7.1875 | 4.5635 | 0.545 | 3.9172 | 346.5 | 1581.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.575 |  | 7.1875 | 4.5635 | 0.5 | 3.5938 | 315 | 1437.5
[11 empty] | Total | 13.0699 | 1701 | 5262.75
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1701 | total F
|  | 1.575 | SAIFI=total F/total customers
|  | 4.8729 | SAIDI=total G/total customers
|  | 3.0939 | CAIDI=SAIDI/SAIFI
|  | 0.99944 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00055627 | ASUI=1-ASAI
|  | 13069.9375 | ENS=total ENS*1000
|  | 12.1018 | AENS=ENS/total customers

## F3_(11-15)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3681.2625
0.1 | 0.1 | 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 25203.775
0.1 | 0.1 |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 6222.325
0.1 | 0.1 |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 6202.3375
0.1 | 0.1 |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | E | 3681.2625
0.1 | 0.1 |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 13648.5875
0.1 | 0.1 |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
0.1 | 0.1 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | Calculation |  |  | 0.535 |  | 1.4175 | 2.6495 | 0.545 | 0.77254 | 117.7 | 311.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 1.4025 | 2.6462 | 0.545 | 0.76436 | 116.6 | 308.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 1.4025 | 2.6462 | 0.545 | 0.76436 | 116.6 | 308.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.59 |  | 1.3575 | 2.3008 | 0.5 | 0.67875 | 118 | 271.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.59 |  | 1.4025 | 2.3771 | 0.5 | 0.70125 | 118 | 280.5
[11 empty] | Total | 3.6813 | 586.9 | 1480.95
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 586.9 | total F
|  | 0.55368 | SAIFI=total F/total customers
|  | 1.3971 | SAIDI=total G/total customers
|  | 2.5233 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015949 | ASUI=1-ASAI
|  | 3681.2625 | ENS=total ENS*1000
|  | 3.4729 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.545 | 5.2129 | 342.1 | 2104.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.545 | 5.2129 | 342.1 | 2104.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.545 | 5.2129 | 342.1 | 2104.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.5 | 4.7825 | 311 | 1913
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.5 | 4.7825 | 311 | 1913
[11 empty] | Total | 25.2038 | 1648.3 | 10138.9
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1648.3 | total F
|  | 1.555 | SAIFI=total F/total customers
|  | 9.565 | SAIDI=total G/total customers
|  | 6.1511 | CAIDI=SAIDI/SAIFI
|  | 0.99891 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0010919 | ASUI=1-ASAI
|  | 25203.775 | ENS=total ENS*1000
|  | 23.7771 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.535 |  | 2.305 | 4.3084 | 0.545 | 1.2562 | 117.7 | 507.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 2.29 | 4.3208 | 0.545 | 1.2481 | 116.6 | 503.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 2.29 | 4.3208 | 0.545 | 1.2481 | 116.6 | 503.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.59 |  | 2.47 | 4.1864 | 0.5 | 1.235 | 118 | 494
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.59 |  | 2.47 | 4.1864 | 0.5 | 1.235 | 118 | 494
[11 empty] | Total | 6.2223 | 586.9 | 2502.7
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 586.9 | total F
|  | 0.55368 | SAIFI=total F/total customers
|  | 2.361 | SAIDI=total G/total customers
|  | 4.2643 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026952 | ASUI=1-ASAI
|  | 6222.325 | ENS=total ENS*1000
|  | 5.8701 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 1.9275 | 1.2395 | 0.545 | 1.0505 | 342.1 | 424.05
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 1.915 | 1.2315 | 0.545 | 1.0437 | 342.1 | 421.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 3.015 | 1.9389 | 0.545 | 1.6432 | 342.1 | 663.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 3.015 | 1.9389 | 0.5 | 1.5075 | 311 | 603
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 1.915 | 1.2315 | 0.5 | 0.9575 | 311 | 383
[11 empty] | Total | 6.2023 | 1648.3 | 2494.65
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1648.3 | total F
|  | 1.555 | SAIFI=total F/total customers
|  | 2.3534 | SAIDI=total G/total customers
|  | 1.5135 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026866 | ASUI=1-ASAI
|  | 6202.3375 | ENS=total ENS*1000
|  | 5.8513 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.535 |  | 1.4175 | 2.6495 | 0.545 | 0.77254 | 117.7 | 311.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 1.4025 | 2.6462 | 0.545 | 0.76436 | 116.6 | 308.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.53 |  | 1.4025 | 2.6462 | 0.545 | 0.76436 | 116.6 | 308.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.59 |  | 1.3575 | 2.3008 | 0.5 | 0.67875 | 118 | 271.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.59 |  | 1.4025 | 2.3771 | 0.5 | 0.70125 | 118 | 280.5
[11 empty] | Total | 3.6813 | 586.9 | 1480.95
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 586.9 | total F
|  | 0.55368 | SAIFI=total F/total customers
|  | 1.3971 | SAIDI=total G/total customers
|  | 2.5233 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015949 | ASUI=1-ASAI
|  | 3681.2625 | ENS=total ENS*1000
|  | 3.4729 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 2.115 | 1.3601 | 0.545 | 1.1527 | 342.1 | 465.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 3.4025 | 2.1881 | 0.545 | 1.8544 | 342.1 | 748.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 5.84 | 3.7556 | 0.545 | 3.1828 | 342.1 | 1284.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.555 |  | 5.84 | 3.7556 | 0.5 | 2.92 | 311 | 1168
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.555 |  | 9.0775 | 5.8376 | 0.5 | 4.5388 | 311 | 1815.5
[11 empty] | Total | 13.6486 | 1648.3 | 5482.15
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 1648.3 | total F
|  | 1.555 | SAIFI=total F/total customers
|  | 5.1718 | SAIDI=total G/total customers
|  | 3.3259 | CAIDI=SAIDI/SAIFI
|  | 0.99941 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00059039 | ASUI=1-ASAI
|  | 13648.5875 | ENS=total ENS*1000
|  | 12.876 | AENS=ENS/total customers

## F4_(18-23)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 4452.675
0.1 | 0.1 | 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | B | 34359.9
0.1 | 0.1 |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 7473.675
0.1 | 0.1 |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 8724.4
0.1 | 0.1 |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | E | 4452.675
0.1 | 0.1 |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 17869.4
0.1 | 0.1 |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
0.1 | 0.1 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
| 0.1 |  |  | x former |  |  | 0 | 0 | 0
| 0.1 |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.545 | 0.74665 | 118.8 | 301.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.5 | 0.685 | 108 | 274
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.5 | 0.7075 | 111 | 283
[11 empty] | Total | 4.4527 | 704.1 | 1792.3
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 704.1 | total F
|  | 0.55008 | SAIFI=total F/total customers
|  | 1.4002 | SAIDI=total G/total customers
|  | 2.5455 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015984 | ASUI=1-ASAI
|  | 4452.675 | ENS=total ENS*1000
|  | 3.4787 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.545 | 5.8887 | 381.7 | 2377.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.545 | 5.8887 | 381.7 | 2377.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.545 | 5.8887 | 381.7 | 2377.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.545 | 5.8887 | 381.7 | 2377.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.5 | 5.4025 | 347 | 2161
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.5 | 5.4025 | 347 | 2161
[11 empty] | Total | 34.3599 | 2220.8 | 13830.4
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2220.8 | total F
|  | 1.735 | SAIFI=total F/total customers
|  | 10.805 | SAIDI=total G/total customers
|  | 6.2277 | CAIDI=SAIDI/SAIFI
|  | 0.99877 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0012334 | ASUI=1-ASAI
|  | 34359.9 | ENS=total ENS*1000
|  | 26.8437 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.545 | 1.2889 | 122.1 | 520.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.545 | 1.2644 | 118.8 | 510.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.545 | 1.2889 | 122.1 | 520.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.545 | 1.2889 | 122.1 | 520.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.5 | 1.16 | 108 | 464
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.5 | 1.1825 | 111 | 473
[11 empty] | Total | 7.4737 | 704.1 | 3008.3
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 704.1 | total F
|  | 0.55008 | SAIFI=total F/total customers
|  | 2.3502 | SAIDI=total G/total customers
|  | 4.2725 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026829 | ASUI=1-ASAI
|  | 7473.675 | ENS=total ENS*1000
|  | 5.8388 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 2.005 | 1.1556 | 0.545 | 1.0927 | 381.7 | 441.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.545 | 1.6922 | 381.7 | 683.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.545 | 1.6922 | 381.7 | 683.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.545 | 1.6922 | 381.7 | 683.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.5 | 1.5525 | 347 | 621
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 2.005 | 1.1556 | 0.5 | 1.0025 | 347 | 401
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
[11 empty] | Total | 8.7244 | 2220.8 | 3512.4
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2220.8 | total F
|  | 1.735 | SAIFI=total F/total customers
|  | 2.7441 | SAIDI=total G/total customers
|  | 1.5816 | CAIDI=SAIDI/SAIFI
|  | 0.99969 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00031325 | ASUI=1-ASAI
|  | 8724.4 | ENS=total ENS*1000
|  | 6.8159 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.545 | 0.74665 | 118.8 | 301.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.5 | 0.685 | 108 | 274
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.5 | 0.7075 | 111 | 283
[11 empty] | Total | 4.4527 | 704.1 | 1792.3
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 704.1 | total F
|  | 0.55008 | SAIFI=total F/total customers
|  | 1.4002 | SAIDI=total G/total customers
|  | 2.5455 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015984 | ASUI=1-ASAI
|  | 4452.675 | ENS=total ENS*1000
|  | 3.4787 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 2.205 | 1.2709 | 0.545 | 1.2017 | 381.7 | 485.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 4.6425 | 2.6758 | 0.545 | 2.5302 | 381.7 | 1021.35
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 4.6425 | 2.6758 | 0.545 | 2.5302 | 381.7 | 1021.35
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 7.08 | 4.0807 | 0.545 | 3.8586 | 381.7 | 1557.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 7.08 | 4.0807 | 0.5 | 3.54 | 347 | 1416
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.735 |  | 8.4175 | 4.8516 | 0.5 | 4.2088 | 347 | 1683.5
[11 empty] | Total | 17.8694 | 2220.8 | 7184.9
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2220.8 | total F
|  | 1.735 | SAIFI=total F/total customers
|  | 5.6132 | SAIDI=total G/total customers
|  | 3.2353 | CAIDI=SAIDI/SAIFI
|  | 0.99936 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00064078 | ASUI=1-ASAI
|  | 17869.4 | ENS=total ENS*1000
|  | 13.9605 | AENS=ENS/total customers

## F7_(32-37)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 4452.9
0.1 | 0.1 | 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 30464.4
0.1 | 0.1 |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 7623
0.1 | 0.1 |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | D | 7861.4
0.1 | 0.1 |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | E | 4452.9
0.1 | 0.1 |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | F | 17759.775
0.1 | 0.1 |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
0.1 | 0.1 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.1 |  |  | Calculation |  |  | 0.54 |  | 1.42 | 2.6296 | 0.545 | 0.7739 | 118.8 | 312.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 1.42 | 2.6296 | 0.545 | 0.7739 | 118.8 | 312.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.52 |  | 1.36 | 2.6154 | 0.545 | 0.7412 | 114.4 | 299.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 1.42 | 2.3667 | 0.545 | 0.7739 | 132 | 312.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 1.36 | 2.2667 | 0.5 | 0.68 | 120 | 272
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 1.42 | 2.3667 | 0.5 | 0.71 | 120 | 284
[11 empty] | Total | 4.4529 | 724 | 1792.4
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 724 | total F
|  | 0.56563 | SAIFI=total F/total customers
|  | 1.4003 | SAIDI=total G/total customers
|  | 2.4757 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015985 | ASUI=1-ASAI
|  | 4452.9 | ENS=total ENS*1000
|  | 3.4788 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.545 | 5.2211 | 343.2 | 2107.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.545 | 5.2211 | 343.2 | 2107.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.545 | 5.2211 | 343.2 | 2107.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.545 | 5.2211 | 343.2 | 2107.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.5 | 4.79 | 312 | 1916
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.5 | 4.79 | 312 | 1916
[11 empty] | Total | 30.4644 | 1996.8 | 12262.4
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1996.8 | total F
|  | 1.56 | SAIFI=total F/total customers
|  | 9.58 | SAIDI=total G/total customers
|  | 6.141 | CAIDI=SAIDI/SAIFI
|  | 0.99891 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0010936 | ASUI=1-ASAI
|  | 30464.4 | ENS=total ENS*1000
|  | 23.8003 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.545 | 1.2644 | 118.8 | 510.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.545 | 1.2644 | 118.8 | 510.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.52 |  | 2.26 | 4.3462 | 0.545 | 1.2317 | 114.4 | 497.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 2.5 | 4.1667 | 0.545 | 1.3625 | 132 | 550
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 2.5 | 4.1667 | 0.5 | 1.25 | 120 | 500
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 2.5 | 4.1667 | 0.5 | 1.25 | 120 | 500
[11 empty] | Total | 7.623 | 724 | 3068
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 724 | total F
|  | 0.56563 | SAIFI=total F/total customers
|  | 2.3969 | SAIDI=total G/total customers
|  | 4.2376 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00027362 | ASUI=1-ASAI
|  | 7623 | ENS=total ENS*1000
|  | 5.9555 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 1.93 | 1.2372 | 0.545 | 1.0519 | 343.2 | 424.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 1.93 | 1.2372 | 0.545 | 1.0519 | 343.2 | 424.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 3.03 | 1.9423 | 0.545 | 1.6513 | 343.2 | 666.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 3.03 | 1.9423 | 0.545 | 1.6513 | 343.2 | 666.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 1.88 | 1.2051 | 0.5 | 0.94 | 312 | 376
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 3.03 | 1.9423 | 0.5 | 1.515 | 312 | 606
[11 empty] | Total | 7.8614 | 1996.8 | 3164.4
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1996.8 | total F
|  | 1.56 | SAIFI=total F/total customers
|  | 2.4722 | SAIDI=total G/total customers
|  | 1.5847 | CAIDI=SAIDI/SAIFI
|  | 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00028221 | ASUI=1-ASAI
|  | 7861.4 | ENS=total ENS*1000
|  | 6.1417 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 1.42 | 2.6296 | 0.545 | 0.7739 | 118.8 | 312.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.54 |  | 1.42 | 2.6296 | 0.545 | 0.7739 | 118.8 | 312.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.52 |  | 1.36 | 2.6154 | 0.545 | 0.7412 | 114.4 | 299.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 1.42 | 2.3667 | 0.545 | 0.7739 | 132 | 312.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 1.36 | 2.2667 | 0.5 | 0.68 | 120 | 272
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.6 |  | 1.42 | 2.3667 | 0.5 | 0.71 | 120 | 284
[11 empty] | Total | 4.4529 | 724 | 1792.4
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 724 | total F
|  | 0.56563 | SAIFI=total F/total customers
|  | 1.4003 | SAIDI=total G/total customers
|  | 2.4757 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015985 | ASUI=1-ASAI
|  | 4452.9 | ENS=total ENS*1000
|  | 3.4788 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 2.1175 | 1.3574 | 0.545 | 1.154 | 343.2 | 465.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 3.4175 | 2.1907 | 0.545 | 1.8625 | 343.2 | 751.85
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 5.855 | 3.7532 | 0.545 | 3.191 | 343.2 | 1288.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 5.855 | 3.7532 | 0.545 | 3.191 | 343.2 | 1288.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.56 |  | 7.1425 | 4.5785 | 0.5 | 3.5713 | 312 | 1428.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.5 | 4.79 | 312 | 1916
[11 empty] | Total | 17.7598 | 1996.8 | 7138.4
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1996.8 | total F
|  | 1.56 | SAIFI=total F/total customers
|  | 5.5769 | SAIDI=total G/total customers
|  | 3.5749 | CAIDI=SAIDI/SAIFI
|  | 0.99936 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00063663 | ASUI=1-ASAI
|  | 17759.775 | ENS=total ENS*1000
|  | 13.8748 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 3737.925 |  | 25795 |  | 6216.925 |  | 6319.875 |  | 3737.925 |  | 13069.938
Feeder 3 | 3681.2625 |  | 25203.775 |  | 6222.325 |  | 6202.3375 |  | 3681.2625 |  | 13648.5875
Feeder 4 | 4452.675 |  | 34359.9 |  | 7473.675 |  | 8724.4 |  | 4452.675 |  | 17869.4
Feeder 7 | 4452.9 |  | 30464.4 |  | 7623 |  | 7861.4 |  | 4452.9 |  | 17759.78
TOTAL | 16324.7625 |  | 115823.075 |  | 27535.925 |  | 29108.0125 |  | 16324.7625 |  | 62347.7055
Analytic | 16.3248 |  | 115.8231 |  | 27.5359 |  | 29.108 |  | 16.3248 |  | 62.3477
Monte Carlo_Code | 16.3239 |  | 115.7568 |  | 27.0406 |  | 29.1038 |  | 16.3222 |  | 61.5684
Deviation | 0.0052834 |  | 0.057221 |  | 1.7988 |  | 0.014472 |  | 0.015697 |  | 1.2499
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 16.3239 | 16.3559 | 16.3401 | 16.3422 |  | 945000 | 115.7568 | 115.8942 | 116.0077 | 115.9257
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 27.0255 | 27.0241 | 27.0406 | 27.0473 |  | 47500 | 29.1274 | 29.1163 | 29.1038 | 29.1089
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 16.3222 | 16.3244 | 16.3353 | 16.33 |  | 1140000 | 61.4478 | 61.4502 | 61.5684 | 61.4268