## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1142.5
0.1 | 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | B | 4567.5
0.1 |  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 3067.5
0.1 |  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 1392.5
0.1 |  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18 | [5 empty] | E | 1142.5
0.1 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 3305
0.1 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | Calculation |  |  | 0.28 |  | 0.29 | 1.0357 | 1 | 0.29 | 0.28 | 0.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.335 | 1.1356 | 1.5 | 0.5025 | 0.295 | 0.335
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.3 |  | 0.35 | 1.1667 | 1 | 0.35 | 0.3 | 0.35
[10 empty] | Total | 1.1425 | 0.875 | 0.975
| 3 | total customers
| 26280 | total (customers*8760)
| 0.875 | total F
| 0.29167 | SAIFI=total F/total customers
| 0.325 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.71e-05 | ASUI=1-ASAI
| 1142.5 | ENS=total ENS*1000
| 380.8333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1 | 1.305 | 0.435 | 1.305
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1.5 | 1.9575 | 0.435 | 1.305
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1 | 1.305 | 0.435 | 1.305
[10 empty] | Total | 4.5675 | 1.305 | 3.915
| 3 | total customers
| 26280 | total (customers*8760)
| 1.305 | total F
| 0.435 | SAIFI=total F/total customers
| 1.305 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014897 | ASUI=1-ASAI
| 4567.5 | ENS=total ENS*1000
| 1522.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.28 |  | 0.84 | 3 | 1 | 0.84 | 0.28 | 0.84
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.885 | 3 | 1.5 | 1.3275 | 0.295 | 0.885
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.3 |  | 0.9 | 3 | 1 | 0.9 | 0.3 | 0.9
[10 empty] | Total | 3.0675 | 0.875 | 2.625
| 3 | total customers
| 26280 | total (customers*8760)
| 0.875 | total F
| 0.29167 | SAIFI=total F/total customers
| 0.875 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 9.9886e-05 | ASUI=1-ASAI
| 3067.5 | ENS=total ENS*1000
| 1022.5 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 18 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | Calculation |  |  | 0.435 |  | 0.3675 | 0.84483 | 1 | 0.3675 | 0.435 | 0.3675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | Calculation |  |  | 0.435 |  | 0.405 | 0.93103 | 1.5 | 0.6075 | 0.435 | 0.405
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 16 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 0.4175 | 0.95977 | 1 | 0.4175 | 0.435 | 0.4175
[10 empty] | Total | 1.3925 | 1.305 | 1.19
| 3 | total customers
| 26280 | total (customers*8760)
| 1.305 | total F
| 0.435 | SAIFI=total F/total customers
| 0.39667 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.5282e-05 | ASUI=1-ASAI
| 1392.5 | ENS=total ENS*1000
| 464.1667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 18 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | Calculation |  |  | 0.435 |  | 0.5675 | 1.3046 | 1 | 0.5675 | 0.435 | 0.5675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | Calculation |  |  | 0.435 |  | 0.955 | 2.1954 | 1.5 | 1.4325 | 0.435 | 0.955
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1 | 1.305 | 0.435 | 1.305
[10 empty] | Total | 3.305 | 1.305 | 2.8275
| 3 | total customers
| 26280 | total (customers*8760)
| 1.305 | total F
| 0.435 | SAIFI=total F/total customers
| 0.9425 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00010759 | ASUI=1-ASAI
| 3305 | ENS=total ENS*1000
| 1101.6667 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 967.5
0.1 | 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | B | 3870
0.1 |  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 2580
0.1 |  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | D | 1182.5
0.1 |  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225 | [5 empty] | E | 967.5
0.1 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 2845
0.1 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | Calculation |  |  | 0.29 |  | 0.3325 | 1.1466 | 1 | 0.3325 | 0.29 | 0.3325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.3475 | 1.178 | 1 | 0.3475 | 0.295 | 0.3475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.275 |  | 0.2875 | 1.0455 | 1 | 0.2875 | 0.275 | 0.2875
[10 empty] | Total | 0.9675 | 0.86 | 0.9675
| 3 | total customers
| 26280 | total (customers*8760)
| 0.86 | total F
| 0.28667 | SAIFI=total F/total customers
| 0.3225 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.6815e-05 | ASUI=1-ASAI
| 967.5 | ENS=total ENS*1000
| 322.5 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
[10 empty] | Total | 3.87 | 1.29 | 3.87
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 1.29 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014726 | ASUI=1-ASAI
| 3870 | ENS=total ENS*1000
| 1290 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.29 |  | 0.87 | 3 | 1 | 0.87 | 0.29 | 0.87
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.885 | 3 | 1 | 0.885 | 0.295 | 0.885
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.275 |  | 0.825 | 3 | 1 | 0.825 | 0.275 | 0.825
[10 empty] | Total | 2.58 | 0.86 | 2.58
| 3 | total customers
| 26280 | total (customers*8760)
| 0.86 | total F
| 0.28667 | SAIFI=total F/total customers
| 0.86 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 9.8174e-05 | ASUI=1-ASAI
| 2580 | ENS=total ENS*1000
| 860 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 49 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.4025 | 0.93605 | 1 | 0.4025 | 0.43 | 0.4025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.415 | 0.96512 | 1 | 0.415 | 0.43 | 0.415
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 47 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 0.365 | 0.84884 | 1 | 0.365 | 0.43 | 0.365
[10 empty] | Total | 1.1825 | 1.29 | 1.1825
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.39417 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.4996e-05 | ASUI=1-ASAI
| 1182.5 | ENS=total ENS*1000
| 394.1667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 49 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.6025 | 1.4012 | 1 | 0.6025 | 0.43 | 0.6025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.9525 | 2.2151 | 1 | 0.9525 | 0.43 | 0.9525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
[10 empty] | Total | 2.845 | 1.29 | 2.845
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.94833 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00010826 | ASUI=1-ASAI
| 2845 | ENS=total ENS*1000
| 948.3333 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1086.25
0.1 | 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 4515
0.1 |  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 3142.5
0.1 |  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 1315
0.1 |  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18 | [5 empty] | E | 1086.25
0.1 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 3427.5
0.1 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | Calculation |  |  | 0.295 |  | 0.2975 | 1.0085 | 1 | 0.2975 | 0.295 | 0.2975
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.31 |  | 0.3425 | 1.1048 | 1 | 0.3425 | 0.31 | 0.3425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.295 |  | 0.2975 | 1.0085 | 1.5 | 0.44625 | 0.295 | 0.2975
[10 empty] | Total | 1.0862 | 0.9 | 0.9375
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9 | total F
| 0.3 | SAIFI=total F/total customers
| 0.3125 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.5674e-05 | ASUI=1-ASAI
| 1086.25 | ENS=total ENS*1000
| 362.0833 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1.5 | 1.935 | 0.43 | 1.29
[10 empty] | Total | 4.515 | 1.29 | 3.87
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 1.29 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014726 | ASUI=1-ASAI
| 4515 | ENS=total ENS*1000
| 1505 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.885 | 3 | 1 | 0.885 | 0.295 | 0.885
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.31 |  | 0.93 | 3 | 1 | 0.93 | 0.31 | 0.93
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.295 |  | 0.885 | 3 | 1.5 | 1.3275 | 0.295 | 0.885
[10 empty] | Total | 3.1425 | 0.9 | 2.7
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9 | total F
| 0.3 | SAIFI=total F/total customers
| 0.9 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00010274 | ASUI=1-ASAI
| 3142.5 | ENS=total ENS*1000
| 1047.5 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 55 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.365 | 0.84884 | 1 | 0.365 | 0.43 | 0.365
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.4025 | 0.93605 | 1 | 0.4025 | 0.43 | 0.4025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 53 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 0.365 | 0.84884 | 1.5 | 0.5475 | 0.43 | 0.365
[10 empty] | Total | 1.315 | 1.29 | 1.1325
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.3775 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.3094e-05 | ASUI=1-ASAI
| 1315 | ENS=total ENS*1000
| 438.3333 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 55 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.5525 | 1.2849 | 1 | 0.5525 | 0.43 | 0.5525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.94 | 2.186 | 1 | 0.94 | 0.43 | 0.94
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1.5 | 1.935 | 0.43 | 1.29
[10 empty] | Total | 3.4275 | 1.29 | 2.7825
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.9275 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00010588 | ASUI=1-ASAI
| 3427.5 | ENS=total ENS*1000
| 1142.5 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 2 | 1142.5 |  | 4567.5 |  | 3067.5 |  | 1392.5 |  | 1142.5 |  | 3305
Feeder 5 | 967.5 |  | 3870 |  | 2580 |  | 1182.5 |  | 967.5 |  | 2845
Feeder 6 | 1086.25 |  | 4515 |  | 3142.5 |  | 1315 |  | 1086.25 |  | 3427.5
TOTAL | 3196.25 |  | 12952.5 |  | 8790 |  | 3890 |  | 3196.25 |  | 9577.5
Analytic | 3.1963 |  | 12.9525 |  | 8.79 |  | 3.89 |  | 3.1963 |  | 9.5775
Monte Carlo_Code | 3.1961 |  | 12.9431 |  | 8.7798 |  | 3.8819 |  | 3.1862 |  | 9.546
Deviation | 0.004693 |  | 0.072573 |  | 0.11604 |  | 0.20823 |  | 0.31443 |  | 0.3289
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 3.2028 | 3.2022 | 3.1977 | 3.1961 |  | 945000 | 12.9542 | 12.9431 | 12.8869 | 12.9474
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 8.7798 | 8.8265 | 8.8137 | 8.8094 |  | 47500 | 3.8819 | 3.8931 | 3.8944 | 3.889
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 3.2038 | 3.1862 | 3.1994 | 3.2048 |  | 1140000 | 9.5945 | 9.5986 | 9.546 | 9.589