## F1_(6-7)
[7 empty] | CASE A | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1349.7875
0.15 | 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 9078.125
0.15 |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 2501.4125
0.15 |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 2894.625
0.15 |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | E | 1349.7875
0.15 |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 9078.125
0.15 |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
0.15 |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0 | 0
0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.6375 | 1.8451 | 0.415 | 0.67956 | 8.875 | 16.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.615 | 1.8197 | 0.415 | 0.67022 | 8.875 | 16.15
[10 empty] | Total | 1.3498 | 17.75 | 32.525
| 20 | total customers
| 175200 | total (customers*8760)
| 17.75 | total F
| 0.8875 | SAIFI=total F/total customers
| 1.6262 | SAIDI=total G/total customers
| 1.8324 | CAIDI=SAIDI/SAIFI
| 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018564 | ASUI=1-ASAI
| 1349.7875 | ENS=total ENS*1000
| 67.4894 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.415 | 4.5391 | 20.125 | 109.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.415 | 4.5391 | 20.125 | 109.375
[10 empty] | Total | 9.0781 | 40.25 | 218.75
| 20 | total customers
| 175200 | total (customers*8760)
| 40.25 | total F
| 2.0125 | SAIFI=total F/total customers
| 10.9375 | SAIDI=total G/total customers
| 5.4348 | CAIDI=SAIDI/SAIFI
| 0.99875 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012486 | ASUI=1-ASAI
| 9078.125 | ENS=total ENS*1000
| 453.9062 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 3.025 | 3.4085 | 0.415 | 1.2554 | 8.875 | 30.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 3.0025 | 3.3831 | 0.415 | 1.246 | 8.875 | 30.025
[10 empty] | Total | 2.5014 | 17.75 | 60.275
| 20 | total customers
| 175200 | total (customers*8760)
| 17.75 | total F
| 0.8875 | SAIFI=total F/total customers
| 3.0137 | SAIDI=total G/total customers
| 3.3958 | CAIDI=SAIDI/SAIFI
| 0.99966 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00034404 | ASUI=1-ASAI
| 2501.4125 | ENS=total ENS*1000
| 125.0706 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 3.4875 | 1.7329 | 0.415 | 1.4473 | 20.125 | 34.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 3.4875 | 1.7329 | 0.415 | 1.4473 | 20.125 | 34.875
[10 empty] | Total | 2.8946 | 40.25 | 69.75
| 20 | total customers
| 175200 | total (customers*8760)
| 40.25 | total F
| 2.0125 | SAIFI=total F/total customers
| 3.4875 | SAIDI=total G/total customers
| 1.7329 | CAIDI=SAIDI/SAIFI
| 0.9996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00039812 | ASUI=1-ASAI
| 2894.625 | ENS=total ENS*1000
| 144.7312 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.6375 | 1.8451 | 0.415 | 0.67956 | 8.875 | 16.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.615 | 1.8197 | 0.415 | 0.67022 | 8.875 | 16.15
[10 empty] | Total | 1.3498 | 17.75 | 32.525
| 20 | total customers
| 175200 | total (customers*8760)
| 17.75 | total F
| 0.8875 | SAIFI=total F/total customers
| 1.6262 | SAIDI=total G/total customers
| 1.8324 | CAIDI=SAIDI/SAIFI
| 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018564 | ASUI=1-ASAI
| 1349.7875 | ENS=total ENS*1000
| 67.4894 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.415 | 4.5391 | 20.125 | 109.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.415 | 4.5391 | 20.125 | 109.375
[10 empty] | Total | 9.0781 | 40.25 | 218.75
| 20 | total customers
| 175200 | total (customers*8760)
| 40.25 | total F
| 2.0125 | SAIFI=total F/total customers
| 10.9375 | SAIDI=total G/total customers
| 5.4348 | CAIDI=SAIDI/SAIFI
| 0.99875 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012486 | ASUI=1-ASAI
| 9078.125 | ENS=total ENS*1000
| 453.9062 | AENS=ENS/total customers

## F3_(16-17)
[7 empty] | CASE A | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1303.1
0.15 | 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 9003.425
0.15 |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | C | 2660.15
0.15 |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 2819.925
0.15 |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 1303.1
0.15 |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 9003.425
0.15 |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
0.15 |  |  | 30 | 0.6 | 0.15 | 0.09 | 0 | 0
0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.6038 | 1.9207 | 0.415 | 0.66556 | 8.35 | 16.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.5362 | 1.8398 | 0.415 | 0.63754 | 8.35 | 15.3625
[10 empty] | Total | 1.3031 | 16.7 | 31.4
| 20 | total customers
| 175200 | total (customers*8760)
| 16.7 | total F
| 0.835 | SAIFI=total F/total customers
| 1.57 | SAIDI=total G/total customers
| 1.8802 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017922 | ASUI=1-ASAI
| 1303.1 | ENS=total ENS*1000
| 65.155 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.415 | 4.5017 | 19.825 | 108.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.415 | 4.5017 | 19.825 | 108.475
[10 empty] | Total | 9.0034 | 39.65 | 216.95
| 20 | total customers
| 175200 | total (customers*8760)
| 39.65 | total F
| 1.9825 | SAIFI=total F/total customers
| 10.8475 | SAIDI=total G/total customers
| 5.4716 | CAIDI=SAIDI/SAIFI
| 0.99876 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012383 | ASUI=1-ASAI
| 9003.425 | ENS=total ENS*1000
| 450.1712 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 3.205 | 3.8383 | 0.415 | 1.3301 | 8.35 | 32.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 3.205 | 3.8383 | 0.415 | 1.3301 | 8.35 | 32.05
[10 empty] | Total | 2.6601 | 16.7 | 64.1
| 20 | total customers
| 175200 | total (customers*8760)
| 16.7 | total F
| 0.835 | SAIFI=total F/total customers
| 3.205 | SAIDI=total G/total customers
| 3.8383 | CAIDI=SAIDI/SAIFI
| 0.99963 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00036587 | ASUI=1-ASAI
| 2660.15 | ENS=total ENS*1000
| 133.0075 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 3.3975 | 1.7137 | 0.415 | 1.41 | 19.825 | 33.975
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 3.3975 | 1.7137 | 0.415 | 1.41 | 19.825 | 33.975
[10 empty] | Total | 2.8199 | 39.65 | 67.95
| 20 | total customers
| 175200 | total (customers*8760)
| 39.65 | total F
| 1.9825 | SAIFI=total F/total customers
| 3.3975 | SAIDI=total G/total customers
| 1.7137 | CAIDI=SAIDI/SAIFI
| 0.99961 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00038784 | ASUI=1-ASAI
| 2819.925 | ENS=total ENS*1000
| 140.9962 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.6038 | 1.9207 | 0.415 | 0.66556 | 8.35 | 16.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.5362 | 1.8398 | 0.415 | 0.63754 | 8.35 | 15.3625
[10 empty] | Total | 1.3031 | 16.7 | 31.4
| 20 | total customers
| 175200 | total (customers*8760)
| 16.7 | total F
| 0.835 | SAIFI=total F/total customers
| 1.57 | SAIDI=total G/total customers
| 1.8802 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017922 | ASUI=1-ASAI
| 1303.1 | ENS=total ENS*1000
| 65.155 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.415 | 4.5017 | 19.825 | 108.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.415 | 4.5017 | 19.825 | 108.475
[10 empty] | Total | 9.0034 | 39.65 | 216.95
| 20 | total customers
| 175200 | total (customers*8760)
| 39.65 | total F
| 1.9825 | SAIFI=total F/total customers
| 10.8475 | SAIDI=total G/total customers
| 5.4716 | CAIDI=SAIDI/SAIFI
| 0.99876 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012383 | ASUI=1-ASAI
| 9003.425 | ENS=total ENS*1000
| 450.1712 | AENS=ENS/total customers

## F4_(24-25)
[7 empty] | CASE A | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1318.6625
0.15 | 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 10132.225
0.15 |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 2501.4125
0.15 |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 2911.225
0.15 |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 1318.6625
0.15 |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 10132.225
0.15 |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
0.15 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
0.15 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.415 | 0.67334 | 7.825 | 16.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.415 | 0.64532 | 7.6 | 15.55
[10 empty] | Total | 1.3187 | 15.425 | 31.775
| 20 | total customers
| 175200 | total (customers*8760)
| 15.425 | total F
| 0.77125 | SAIFI=total F/total customers
| 1.5887 | SAIDI=total G/total customers
| 2.06 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018136 | ASUI=1-ASAI
| 1318.6625 | ENS=total ENS*1000
| 65.9331 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.415 | 5.0661 | 22.025 | 122.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.415 | 5.0661 | 22.025 | 122.075
[10 empty] | Total | 10.1322 | 44.05 | 244.15
| 20 | total customers
| 175200 | total (customers*8760)
| 44.05 | total F
| 2.2025 | SAIFI=total F/total customers
| 12.2075 | SAIDI=total G/total customers
| 5.5426 | CAIDI=SAIDI/SAIFI
| 0.99861 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0013936 | ASUI=1-ASAI
| 10132.225 | ENS=total ENS*1000
| 506.6113 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.415 | 1.2647 | 7.825 | 30.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.415 | 1.2367 | 7.6 | 29.8
[10 empty] | Total | 2.5014 | 15.425 | 60.275
| 20 | total customers
| 175200 | total (customers*8760)
| 15.425 | total F
| 0.77125 | SAIFI=total F/total customers
| 3.0137 | SAIDI=total G/total customers
| 3.9076 | CAIDI=SAIDI/SAIFI
| 0.99966 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00034404 | ASUI=1-ASAI
| 2501.4125 | ENS=total ENS*1000
| 125.0706 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.415 | 1.4556 | 22.025 | 35.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.415 | 1.4556 | 22.025 | 35.075
[10 empty] | Total | 2.9112 | 44.05 | 70.15
| 20 | total customers
| 175200 | total (customers*8760)
| 44.05 | total F
| 2.2025 | SAIFI=total F/total customers
| 3.5075 | SAIDI=total G/total customers
| 1.5925 | CAIDI=SAIDI/SAIFI
| 0.9996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0004004 | ASUI=1-ASAI
| 2911.225 | ENS=total ENS*1000
| 145.5612 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.415 | 0.67334 | 7.825 | 16.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.415 | 0.64532 | 7.6 | 15.55
[10 empty] | Total | 1.3187 | 15.425 | 31.775
| 20 | total customers
| 175200 | total (customers*8760)
| 15.425 | total F
| 0.77125 | SAIFI=total F/total customers
| 1.5887 | SAIDI=total G/total customers
| 2.06 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018136 | ASUI=1-ASAI
| 1318.6625 | ENS=total ENS*1000
| 65.9331 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.415 | 5.0661 | 22.025 | 122.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.415 | 5.0661 | 22.025 | 122.075
[10 empty] | Total | 10.1322 | 44.05 | 244.15
| 20 | total customers
| 175200 | total (customers*8760)
| 44.05 | total F
| 2.2025 | SAIFI=total F/total customers
| 12.2075 | SAIDI=total G/total customers
| 5.5426 | CAIDI=SAIDI/SAIFI
| 0.99861 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0013936 | ASUI=1-ASAI
| 10132.225 | ENS=total ENS*1000
| 506.6113 | AENS=ENS/total customers

## F7_(38)
[7 empty] | CASE A | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 639.1
0.15 | 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 4511.05
0.15 |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | C | 1348.75
0.15 |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | D | 1419.3
0.15 |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | E | 639.1
0.15 |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | F | 4511.05
0.15 |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 66 | 0.8 | 0.15 | 0.12 | 0 | 0
0.15 |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.54 | 1.8118 | 0.415 | 0.6391 | 8.5 | 15.4
[10 empty] | Total | 0.6391 | 8.5 | 15.4
| 10 | total customers
| 87600 | total (customers*8760)
| 8.5 | total F
| 0.85 | SAIFI=total F/total customers
| 1.54 | SAIDI=total G/total customers
| 1.8118 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001758 | ASUI=1-ASAI
| 639.1 | ENS=total ENS*1000
| 63.91 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.415 | 4.511 | 19.9 | 108.7
[10 empty] | Total | 4.511 | 19.9 | 108.7
| 10 | total customers
| 87600 | total (customers*8760)
| 19.9 | total F
| 1.99 | SAIFI=total F/total customers
| 10.87 | SAIDI=total G/total customers
| 5.4623 | CAIDI=SAIDI/SAIFI
| 0.99876 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012409 | ASUI=1-ASAI
| 4511.05 | ENS=total ENS*1000
| 451.105 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 3.25 | 3.8235 | 0.415 | 1.3487 | 8.5 | 32.5
[10 empty] | Total | 1.3487 | 8.5 | 32.5
| 10 | total customers
| 87600 | total (customers*8760)
| 8.5 | total F
| 0.85 | SAIFI=total F/total customers
| 3.25 | SAIDI=total G/total customers
| 3.8235 | CAIDI=SAIDI/SAIFI
| 0.99963 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.000371 | ASUI=1-ASAI
| 1348.75 | ENS=total ENS*1000
| 134.875 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 3.42 | 1.7186 | 0.415 | 1.4193 | 19.9 | 34.2
[10 empty] | Total | 1.4193 | 19.9 | 34.2
| 10 | total customers
| 87600 | total (customers*8760)
| 19.9 | total F
| 1.99 | SAIFI=total F/total customers
| 3.42 | SAIDI=total G/total customers
| 1.7186 | CAIDI=SAIDI/SAIFI
| 0.99961 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00039041 | ASUI=1-ASAI
| 1419.3 | ENS=total ENS*1000
| 141.93 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.54 | 1.8118 | 0.415 | 0.6391 | 8.5 | 15.4
[10 empty] | Total | 0.6391 | 8.5 | 15.4
| 10 | total customers
| 87600 | total (customers*8760)
| 8.5 | total F
| 0.85 | SAIFI=total F/total customers
| 1.54 | SAIDI=total G/total customers
| 1.8118 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001758 | ASUI=1-ASAI
| 639.1 | ENS=total ENS*1000
| 63.91 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.415 | 4.511 | 19.9 | 108.7
[10 empty] | Total | 4.511 | 19.9 | 108.7
| 10 | total customers
| 87600 | total (customers*8760)
| 19.9 | total F
| 1.99 | SAIFI=total F/total customers
| 10.87 | SAIDI=total G/total customers
| 5.4623 | CAIDI=SAIDI/SAIFI
| 0.99876 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012409 | ASUI=1-ASAI
| 4511.05 | ENS=total ENS*1000
| 451.105 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 1349.7875 | 20 | 9078.125 | 20 | 2501.4125 | 20 | 2894.625 | 20 | 1349.7875 | 20 | 9078.125 | 20
Feeder 3 | 1303.1 | 20 | 9003.425 | 20 | 2660.15 | 20 | 2819.925 | 20 | 1303.1 | 20 | 9003.425 | 20
Feeder 4 | 1318.6625 | 20 | 10132.225 | 20 | 2501.4125 | 20 | 2911.225 | 20 | 1318.6625 | 20 | 10132.225 | 20
Feeder 7 | 639.1 | 10 | 4511.05 | 10 | 1348.75 | 10 | 1419.3 | 10 | 639.1 | 10 | 4511.05 | 10
TOTAL | 4610.65 | 70 | 32724.825 | 70 | 9011.725 | 70 | 10045.075 | 70 | 4610.65 | 70 | 32724.825 | 70
Analytic | 4.6106 |  | 32.7248 |  | 9.0117 |  | 10.0451 |  | 4.6106 |  | 32.7248
Monte Carlo_Code | 4.6104 |  | 32.7246 |  | 8.9246 |  | 10.0383 |  | 4.6065 |  | 32.7237
Deviation | 0.0054222 |  | 0.00068755 |  | 0.9668 |  | 0.067446 |  | 0.090009 |  | 0.0034378
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 4.6441 | 4.6104 | 4.6248 | 4.6158 |  | 945000 | 32.7925 | 32.7143 | 32.7362 | 32.7246
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 8.9227 | 8.9143 | 8.9246 | 8.909 |  | 47500 | 10.0218 | 10.0535 | 10.0341 | 10.0383
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 4.654 | 4.6065 | 4.6092 | 4.6079 |  | 1140000 | 32.7237 | 32.7272 | 32.744 | 32.7258