## F1_(1-5)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 4266.8875
0.1 | 0.15 | 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 29312.5
0.1 | 0.15 |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 7985.3875
0.1 | 0.15 |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 7241.4375
0.1 | 0.15 |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | E | 4266.8875
0.1 | 0.15 |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 15100.7812
0.1 | 0.15 |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
0.1 | 0.15 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | Calculation |  |  | 0.745 |  | 1.5475 | 2.0772 | 0.545 | 0.84339 | 163.9 | 340.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7675 |  | 1.615 | 2.1042 | 0.545 | 0.88018 | 168.85 | 355.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 1.5475 | 2.0772 | 0.545 | 0.84339 | 163.9 | 340.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.8875 |  | 1.6375 | 1.8451 | 0.545 | 0.89244 | 195.25 | 360.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.8875 |  | 1.615 | 1.8197 | 0.5 | 0.8075 | 177.5 | 323
[11 empty] | Total | 4.2669 | 869.4 | 1719.45
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 869.4 | total F
|  | 0.805 | SAIFI=total F/total customers
|  | 1.5921 | SAIDI=total G/total customers
|  | 1.9777 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00018174 | ASUI=1-ASAI
|  | 4266.8875 | ENS=total ENS*1000
|  | 3.9508 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.545 | 5.9609 | 442.75 | 2406.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.545 | 5.9609 | 442.75 | 2406.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.545 | 5.9609 | 442.75 | 2406.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.545 | 5.9609 | 442.75 | 2406.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.5 | 5.4688 | 402.5 | 2187.5
[11 empty] | Total | 29.3125 | 2173.5 | 11812.5
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 2173.5 | total F
|  | 2.0125 | SAIFI=total F/total customers
|  | 10.9375 | SAIDI=total G/total customers
|  | 5.4348 | CAIDI=SAIDI/SAIFI
|  | 0.99875 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0012486 | ASUI=1-ASAI
|  | 29312.5 | ENS=total ENS*1000
|  | 27.1412 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 2.935 | 3.9396 | 0.545 | 1.5996 | 163.9 | 645.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7675 |  | 3.0025 | 3.9121 | 0.545 | 1.6364 | 168.85 | 660.55
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 2.935 | 3.9396 | 0.545 | 1.5996 | 163.9 | 645.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.8875 |  | 3.025 | 3.4085 | 0.545 | 1.6486 | 195.25 | 665.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.8875 |  | 3.0025 | 3.3831 | 0.5 | 1.5012 | 177.5 | 600.5
[11 empty] | Total | 7.9854 | 869.4 | 3217.95
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 869.4 | total F
|  | 0.805 | SAIFI=total F/total customers
|  | 2.9796 | SAIDI=total G/total customers
|  | 3.7013 | CAIDI=SAIDI/SAIFI
|  | 0.99966 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00034014 | ASUI=1-ASAI
|  | 7985.3875 | ENS=total ENS*1000
|  | 7.3939 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 2.1812 | 1.0839 | 0.545 | 1.1888 | 442.75 | 479.875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 2.2375 | 1.1118 | 0.545 | 1.2194 | 442.75 | 492.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 2.1812 | 1.0839 | 0.545 | 1.1888 | 442.75 | 479.875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 3.4875 | 1.7329 | 0.545 | 1.9007 | 442.75 | 767.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 3.4875 | 1.7329 | 0.5 | 1.7437 | 402.5 | 697.5
[11 empty] | Total | 7.2414 | 2173.5 | 2916.75
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 2173.5 | total F
|  | 2.0125 | SAIFI=total F/total customers
|  | 2.7007 | SAIDI=total G/total customers
|  | 1.342 | CAIDI=SAIDI/SAIFI
|  | 0.99969 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0003083 | ASUI=1-ASAI
|  | 7241.4375 | ENS=total ENS*1000
|  | 6.705 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 1.5475 | 2.0772 | 0.545 | 0.84339 | 163.9 | 340.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7675 |  | 1.615 | 2.1042 | 0.545 | 0.88018 | 168.85 | 355.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 1.5475 | 2.0772 | 0.545 | 0.84339 | 163.9 | 340.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.8875 |  | 1.6375 | 1.8451 | 0.545 | 0.89244 | 195.25 | 360.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.8875 |  | 1.615 | 1.8197 | 0.5 | 0.8075 | 177.5 | 323
[11 empty] | Total | 4.2669 | 869.4 | 1719.45
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 869.4 | total F
|  | 0.805 | SAIFI=total F/total customers
|  | 1.5921 | SAIDI=total G/total customers
|  | 1.9777 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00018174 | ASUI=1-ASAI
|  | 4266.8875 | ENS=total ENS*1000
|  | 3.9508 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 2.4625 | 1.2236 | 0.545 | 1.3421 | 442.75 | 541.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 3.9937 | 1.9845 | 0.545 | 2.1766 | 442.75 | 878.625
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 5.4687 | 2.7174 | 0.545 | 2.9805 | 442.75 | 1203.125
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 8.2313 | 4.0901 | 0.545 | 4.486 | 442.75 | 1810.875
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.0125 |  | 8.2313 | 4.0901 | 0.5 | 4.1156 | 402.5 | 1646.25
[11 empty] | Total | 15.1008 | 2173.5 | 6080.625
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 2173.5 | total F
|  | 2.0125 | SAIFI=total F/total customers
|  | 5.6302 | SAIDI=total G/total customers
|  | 2.7976 | CAIDI=SAIDI/SAIFI
|  | 0.99936 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00064272 | ASUI=1-ASAI
|  | 15100.7812 | ENS=total ENS*1000
|  | 13.9822 | AENS=ENS/total customers

## F3_(11-15)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 4204.3938
0.1 | 0.15 | 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 28583.1625
0.1 | 0.15 |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | C | 8015.9875
0.1 | 0.15 |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 7094.3812
0.1 | 0.15 |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 4204.3938
0.1 | 0.15 |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 15587.1312
0.1 | 0.15 |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
0.1 | 0.15 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | Calculation |  |  | 0.7525 |  | 1.6262 | 2.1611 | 0.545 | 0.88631 | 165.55 | 357.775
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 1.6038 | 2.1527 | 0.545 | 0.87404 | 163.9 | 352.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 1.6038 | 2.1527 | 0.545 | 0.87404 | 163.9 | 352.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.835 |  | 1.5362 | 1.8398 | 0.5 | 0.76812 | 167 | 307.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.835 |  | 1.6038 | 1.9207 | 0.5 | 0.80188 | 167 | 320.75
[11 empty] | Total | 4.2044 | 827.35 | 1691.425
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 827.35 | total F
|  | 0.78052 | SAIFI=total F/total customers
|  | 1.5957 | SAIDI=total G/total customers
|  | 2.0444 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00018216 | ASUI=1-ASAI
|  | 4204.3938 | ENS=total ENS*1000
|  | 3.9664 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.545 | 5.9119 | 436.15 | 2386.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.545 | 5.9119 | 436.15 | 2386.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.545 | 5.9119 | 436.15 | 2386.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.5 | 5.4238 | 396.5 | 2169.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.5 | 5.4238 | 396.5 | 2169.5
[11 empty] | Total | 28.5832 | 2101.45 | 11498.35
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 2101.45 | total F
|  | 1.9825 | SAIFI=total F/total customers
|  | 10.8475 | SAIDI=total G/total customers
|  | 5.4716 | CAIDI=SAIDI/SAIFI
|  | 0.99876 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0012383 | ASUI=1-ASAI
|  | 28583.1625 | ENS=total ENS*1000
|  | 26.9652 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7525 |  | 2.9575 | 3.9302 | 0.545 | 1.6118 | 165.55 | 650.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 2.935 | 3.9396 | 0.545 | 1.5996 | 163.9 | 645.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 2.935 | 3.9396 | 0.545 | 1.5996 | 163.9 | 645.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.835 |  | 3.205 | 3.8383 | 0.5 | 1.6025 | 167 | 641
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.835 |  | 3.205 | 3.8383 | 0.5 | 1.6025 | 167 | 641
[11 empty] | Total | 8.016 | 827.35 | 3224.05
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 827.35 | total F
|  | 0.78052 | SAIFI=total F/total customers
|  | 3.0416 | SAIDI=total G/total customers
|  | 3.8968 | CAIDI=SAIDI/SAIFI
|  | 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00034721 | ASUI=1-ASAI
|  | 8015.9875 | ENS=total ENS*1000
|  | 7.5623 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 2.2412 | 1.1305 | 0.545 | 1.2215 | 436.15 | 493.075
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 2.2225 | 1.1211 | 0.545 | 1.2113 | 436.15 | 488.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 3.3975 | 1.7137 | 0.545 | 1.8516 | 436.15 | 747.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 3.3975 | 1.7137 | 0.5 | 1.6987 | 396.5 | 679.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 2.2225 | 1.1211 | 0.5 | 1.1112 | 396.5 | 444.5
[11 empty] | Total | 7.0944 | 2101.45 | 2853.475
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 2101.45 | total F
|  | 1.9825 | SAIFI=total F/total customers
|  | 2.692 | SAIDI=total G/total customers
|  | 1.3579 | CAIDI=SAIDI/SAIFI
|  | 0.99969 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0003073 | ASUI=1-ASAI
|  | 7094.3812 | ENS=total ENS*1000
|  | 6.6928 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7525 |  | 1.6262 | 2.1611 | 0.545 | 0.88631 | 165.55 | 357.775
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 1.6038 | 2.1527 | 0.545 | 0.87404 | 163.9 | 352.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.745 |  | 1.6038 | 2.1527 | 0.545 | 0.87404 | 163.9 | 352.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.835 |  | 1.5362 | 1.8398 | 0.5 | 0.76812 | 167 | 307.25
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.835 |  | 1.6038 | 1.9207 | 0.5 | 0.80188 | 167 | 320.75
[11 empty] | Total | 4.2044 | 827.35 | 1691.425
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 827.35 | total F
|  | 0.78052 | SAIFI=total F/total customers
|  | 1.5957 | SAIDI=total G/total customers
|  | 2.0444 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00018216 | ASUI=1-ASAI
|  | 4204.3938 | ENS=total ENS*1000
|  | 3.9664 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 2.5225 | 1.2724 | 0.545 | 1.3748 | 436.15 | 554.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 3.9787 | 2.0069 | 0.545 | 2.1684 | 436.15 | 875.325
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 6.685 | 3.372 | 0.545 | 3.6433 | 436.15 | 1470.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.9825 |  | 6.685 | 3.372 | 0.5 | 3.3425 | 396.5 | 1337
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.9825 |  | 10.1162 | 5.1028 | 0.5 | 5.0581 | 396.5 | 2023.25
[11 empty] | Total | 15.5871 | 2101.45 | 6261.225
|  | 1060 | total customers
|  | 9285600 | total (customers*8760)
|  | 2101.45 | total F
|  | 1.9825 | SAIFI=total F/total customers
|  | 5.9068 | SAIDI=total G/total customers
|  | 2.9795 | CAIDI=SAIDI/SAIFI
|  | 0.99933 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00067429 | ASUI=1-ASAI
|  | 15587.1312 | ENS=total ENS*1000
|  | 14.7048 | AENS=ENS/total customers

## F4_(18-23)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 5089.0125
0.1 | 0.15 | 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 38819.85
0.1 | 0.15 |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 9620.5125
0.1 | 0.15 |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 9925.975
0.1 | 0.15 |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 5089.0125
0.1 | 0.15 |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 20449.1
0.1 | 0.15 |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
0.1 | 0.15 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
| 0.15 |  |  | x former |  |  | 0 | 0 | 0
| 0.15 |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.545 | 0.84747 | 167.2 | 342.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.5 | 0.7775 | 152 | 311
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.5 | 0.81125 | 156.5 | 324.5
[11 empty] | Total | 5.089 | 992.15 | 2048.45
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 992.15 | total F
|  | 0.77512 | SAIFI=total F/total customers
|  | 1.6004 | SAIDI=total G/total customers
|  | 2.0647 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00018269 | ASUI=1-ASAI
|  | 5089.0125 | ENS=total ENS*1000
|  | 3.9758 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.545 | 6.6531 | 484.55 | 2685.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.545 | 6.6531 | 484.55 | 2685.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.545 | 6.6531 | 484.55 | 2685.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.545 | 6.6531 | 484.55 | 2685.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.5 | 6.1037 | 440.5 | 2441.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.5 | 6.1037 | 440.5 | 2441.5
[11 empty] | Total | 38.8198 | 2819.2 | 15625.6
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2819.2 | total F
|  | 2.2025 | SAIFI=total F/total customers
|  | 12.2075 | SAIDI=total G/total customers
|  | 5.5426 | CAIDI=SAIDI/SAIFI
|  | 0.99861 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0013936 | ASUI=1-ASAI
|  | 38819.85 | ENS=total ENS*1000
|  | 30.328 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.545 | 1.6609 | 172.15 | 670.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.545 | 1.6241 | 167.2 | 655.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.545 | 1.6609 | 172.15 | 670.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.545 | 1.6609 | 172.15 | 670.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.5 | 1.49 | 152 | 596
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.5 | 1.5237 | 156.5 | 609.5
[11 empty] | Total | 9.6205 | 992.15 | 3872.45
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 992.15 | total F
|  | 0.77512 | SAIFI=total F/total customers
|  | 3.0254 | SAIDI=total G/total customers
|  | 3.9031 | CAIDI=SAIDI/SAIFI
|  | 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00034536 | ASUI=1-ASAI
|  | 9620.5125 | ENS=total ENS*1000
|  | 7.516 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 2.3325 | 1.059 | 0.545 | 1.2712 | 484.55 | 513.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.545 | 1.9116 | 484.55 | 771.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.545 | 1.9116 | 484.55 | 771.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.545 | 1.9116 | 484.55 | 771.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.5 | 1.7537 | 440.5 | 701.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 2.3325 | 1.059 | 0.5 | 1.1662 | 440.5 | 466.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
[11 empty] | Total | 9.926 | 2819.2 | 3996.1
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2819.2 | total F
|  | 2.2025 | SAIFI=total F/total customers
|  | 3.122 | SAIDI=total G/total customers
|  | 1.4175 | CAIDI=SAIDI/SAIFI
|  | 0.99964 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00035639 | ASUI=1-ASAI
|  | 9925.975 | ENS=total ENS*1000
|  | 7.7547 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.545 | 0.84747 | 167.2 | 342.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.5 | 0.7775 | 152 | 311
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.5 | 0.81125 | 156.5 | 324.5
[11 empty] | Total | 5.089 | 992.15 | 2048.45
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 992.15 | total F
|  | 0.77512 | SAIFI=total F/total customers
|  | 1.6004 | SAIDI=total G/total customers
|  | 2.0647 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00018269 | ASUI=1-ASAI
|  | 5089.0125 | ENS=total ENS*1000
|  | 3.9758 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 2.6325 | 1.1952 | 0.545 | 1.4347 | 484.55 | 579.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 5.3387 | 2.424 | 0.545 | 2.9096 | 484.55 | 1174.525
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 5.3387 | 2.424 | 0.545 | 2.9096 | 484.55 | 1174.525
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 8.045 | 3.6527 | 0.545 | 4.3845 | 484.55 | 1769.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 8.045 | 3.6527 | 0.5 | 4.0225 | 440.5 | 1609
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 2.2025 |  | 9.5763 | 4.3479 | 0.5 | 4.7881 | 440.5 | 1915.25
[11 empty] | Total | 20.4491 | 2819.2 | 8222.35
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2819.2 | total F
|  | 2.2025 | SAIFI=total F/total customers
|  | 6.4237 | SAIDI=total G/total customers
|  | 2.9166 | CAIDI=SAIDI/SAIFI
|  | 0.99927 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0007333 | ASUI=1-ASAI
|  | 20449.1 | ENS=total ENS*1000
|  | 15.9759 | AENS=ENS/total customers

## F7_(32-37)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.1 | 0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 5089.35
0.1 | 0.15 | 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 34566.6
0.1 | 0.15 |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | C | 9844.5
0.1 | 0.15 |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | D | 8969.85
0.1 | 0.15 |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | E | 5089.35
0.1 | 0.15 |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | F | 20385.5375
0.1 | 0.15 |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
0.1 | 0.15 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.1 | 0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | x former |  |  | 0 | 0 | 0
0.1 | 0.15 |  |  | Calculation |  |  | 0.76 |  | 1.63 | 2.1447 | 0.545 | 0.88835 | 167.2 | 358.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 1.63 | 2.1447 | 0.545 | 0.88835 | 167.2 | 358.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.73 |  | 1.54 | 2.1096 | 0.545 | 0.8393 | 160.6 | 338.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 1.63 | 1.9176 | 0.545 | 0.88835 | 187 | 358.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 1.54 | 1.8118 | 0.5 | 0.77 | 170 | 308
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 1.63 | 1.9176 | 0.5 | 0.815 | 170 | 326
[11 empty] | Total | 5.0893 | 1022 | 2048.6
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1022 | total F
|  | 0.79844 | SAIFI=total F/total customers
|  | 1.6005 | SAIDI=total G/total customers
|  | 2.0045 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0001827 | ASUI=1-ASAI
|  | 5089.35 | ENS=total ENS*1000
|  | 3.9761 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.545 | 5.9242 | 437.8 | 2391.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.545 | 5.9242 | 437.8 | 2391.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.545 | 5.9242 | 437.8 | 2391.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.545 | 5.9242 | 437.8 | 2391.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.5 | 5.435 | 398 | 2174
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.5 | 5.435 | 398 | 2174
[11 empty] | Total | 34.5666 | 2547.2 | 13913.6
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2547.2 | total F
|  | 1.99 | SAIFI=total F/total customers
|  | 10.87 | SAIDI=total G/total customers
|  | 5.4623 | CAIDI=SAIDI/SAIFI
|  | 0.99876 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0012409 | ASUI=1-ASAI
|  | 34566.6 | ENS=total ENS*1000
|  | 27.0052 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.545 | 1.6241 | 167.2 | 655.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.545 | 1.6241 | 167.2 | 655.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.73 |  | 2.89 | 3.9589 | 0.545 | 1.575 | 160.6 | 635.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 3.25 | 3.8235 | 0.545 | 1.7712 | 187 | 715
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 3.25 | 3.8235 | 0.5 | 1.625 | 170 | 650
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 3.25 | 3.8235 | 0.5 | 1.625 | 170 | 650
[11 empty] | Total | 9.8445 | 1022 | 3962
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1022 | total F
|  | 0.79844 | SAIFI=total F/total customers
|  | 3.0953 | SAIDI=total G/total customers
|  | 3.8767 | CAIDI=SAIDI/SAIFI
|  | 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00035335 | ASUI=1-ASAI
|  | 9844.5 | ENS=total ENS*1000
|  | 7.691 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 2.245 | 1.1281 | 0.545 | 1.2235 | 437.8 | 493.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 2.245 | 1.1281 | 0.545 | 1.2235 | 437.8 | 493.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 3.42 | 1.7186 | 0.545 | 1.8639 | 437.8 | 752.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 3.42 | 1.7186 | 0.545 | 1.8639 | 437.8 | 752.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 2.17 | 1.0905 | 0.5 | 1.085 | 398 | 434
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 3.42 | 1.7186 | 0.5 | 1.71 | 398 | 684
[11 empty] | Total | 8.9698 | 2547.2 | 3610.6
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2547.2 | total F
|  | 1.99 | SAIFI=total F/total customers
|  | 2.8208 | SAIDI=total G/total customers
|  | 1.4175 | CAIDI=SAIDI/SAIFI
|  | 0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00032201 | ASUI=1-ASAI
|  | 8969.85 | ENS=total ENS*1000
|  | 7.0077 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 1.63 | 2.1447 | 0.545 | 0.88835 | 167.2 | 358.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.76 |  | 1.63 | 2.1447 | 0.545 | 0.88835 | 167.2 | 358.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.73 |  | 1.54 | 2.1096 | 0.545 | 0.8393 | 160.6 | 338.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 1.63 | 1.9176 | 0.545 | 0.88835 | 187 | 358.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 1.54 | 1.8118 | 0.5 | 0.77 | 170 | 308
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 1.63 | 1.9176 | 0.5 | 0.815 | 170 | 326
[11 empty] | Total | 5.0893 | 1022 | 2048.6
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 1022 | total F
|  | 0.79844 | SAIFI=total F/total customers
|  | 1.6005 | SAIDI=total G/total customers
|  | 2.0045 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0001827 | ASUI=1-ASAI
|  | 5089.35 | ENS=total ENS*1000
|  | 3.9761 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 2.5262 | 1.2695 | 0.545 | 1.3768 | 437.8 | 555.775
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 4.0012 | 2.0107 | 0.545 | 2.1807 | 437.8 | 880.275
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 6.7075 | 3.3706 | 0.545 | 3.6556 | 437.8 | 1475.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 6.7075 | 3.3706 | 0.545 | 3.6556 | 437.8 | 1475.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  |  | Calculation |  |  | 1.99 |  | 8.1638 | 4.1024 | 0.5 | 4.0819 | 398 | 1632.75
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | x former |  |  | 0.1 | 10 | 1
|  |  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.5 | 5.435 | 398 | 2174
[11 empty] | Total | 20.3855 | 2547.2 | 8194.1
|  | 1280 | total customers
|  | 11212800 | total (customers*8760)
|  | 2547.2 | total F
|  | 1.99 | SAIFI=total F/total customers
|  | 6.4016 | SAIDI=total G/total customers
|  | 3.2169 | CAIDI=SAIDI/SAIFI
|  | 0.99927 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00073078 | ASUI=1-ASAI
|  | 20385.5375 | ENS=total ENS*1000
|  | 15.9262 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 4266.8875 |  | 29312.5 |  | 7985.3875 |  | 7241.4375 |  | 4266.8875 |  | 15100.781
Feeder 3 | 4204.3975 |  | 28583.1625 |  | 8015.9875 |  | 7094.3813 |  | 4204.3975 |  | 15587.1313
Feeder 4 | 5089.013 |  | 38819.85 |  | 9620.513 |  | 9925.975 |  | 5089.013 |  | 20449.1
Feeder 7 | 5089.35 |  | 34566.6 |  | 9844.5 |  | 8969.85 |  | 5089.35 |  | 20385.54
TOTAL | 18649.648 |  | 131282.1125 |  | 35466.388 |  | 33231.6438 |  | 18649.648 |  | 71522.5523
Analytic | 18.6496 |  | 131.2821 |  | 35.4664 |  | 33.2316 |  | 18.6496 |  | 71.5226
Monte Carlo_Code | 18.6428 |  | 131.2403 |  | 34.7024 |  | 33.2264 |  | 18.644 |  | 70.6859
Deviation | 0.036719 |  | 0.031849 |  | 2.1541 |  | 0.015779 |  | 0.030285 |  | 1.1698
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 18.6428 | 18.6824 | 18.6302 | 18.6734 |  | 945000 | 131.2403 | 131.3955 | 131.2825 | 131.2537
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 34.7322 | 34.7199 | 34.7024 | 34.7282 |  | 47500 | 33.2242 | 33.2255 | 33.2264 | 33.2259
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 18.644 | 18.6424 | 18.6185 | 18.6487 |  | 1140000 | 70.5332 | 70.6504 | 70.6859 | 70.6229