## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1713.75
0.15 | 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 6851.25
0.15 |  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 4601.25
0.15 |  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | D | 2088.75
0.15 |  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27 | [5 empty] | E | 1713.75
0.15 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4957.5
0.15 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | Calculation |  |  | 0.42 |  | 0.435 | 1.0357 | 1 | 0.435 | 0.42 | 0.435
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 0.5025 | 1.1356 | 1.5 | 0.75375 | 0.4425 | 0.5025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.45 |  | 0.525 | 1.1667 | 1 | 0.525 | 0.45 | 0.525
[10 empty] | Total | 1.7137 | 1.3125 | 1.4625
| 3 | total customers
| 26280 | total (customers*8760)
| 1.3125 | total F
| 0.4375 | SAIFI=total F/total customers
| 0.4875 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.5651e-05 | ASUI=1-ASAI
| 1713.75 | ENS=total ENS*1000
| 571.25 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 1.9575 | 3 | 1 | 1.9575 | 0.6525 | 1.9575
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 1.9575 | 3 | 1.5 | 2.9363 | 0.6525 | 1.9575
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 1.9575 | 3 | 1 | 1.9575 | 0.6525 | 1.9575
[10 empty] | Total | 6.8513 | 1.9575 | 5.8725
| 3 | total customers
| 26280 | total (customers*8760)
| 1.9575 | total F
| 0.6525 | SAIFI=total F/total customers
| 1.9575 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99978 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022346 | ASUI=1-ASAI
| 6851.25 | ENS=total ENS*1000
| 2283.75 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.42 |  | 1.26 | 3 | 1 | 1.26 | 0.42 | 1.26
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 1.3275 | 3 | 1.5 | 1.9912 | 0.4425 | 1.3275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.45 |  | 1.35 | 3 | 1 | 1.35 | 0.45 | 1.35
[10 empty] | Total | 4.6013 | 1.3125 | 3.9375
| 3 | total customers
| 26280 | total (customers*8760)
| 1.3125 | total F
| 0.4375 | SAIFI=total F/total customers
| 1.3125 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014983 | ASUI=1-ASAI
| 4601.25 | ENS=total ENS*1000
| 1533.75 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 18 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | Calculation |  |  | 0.6525 |  | 0.55125 | 0.84483 | 1 | 0.55125 | 0.6525 | 0.55125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | Calculation |  |  | 0.6525 |  | 0.6075 | 0.93103 | 1.5 | 0.91125 | 0.6525 | 0.6075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 0.62625 | 0.95977 | 1 | 0.62625 | 0.6525 | 0.62625
[10 empty] | Total | 2.0888 | 1.9575 | 1.785
| 3 | total customers
| 26280 | total (customers*8760)
| 1.9575 | total F
| 0.6525 | SAIFI=total F/total customers
| 0.595 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.7922e-05 | ASUI=1-ASAI
| 2088.75 | ENS=total ENS*1000
| 696.25 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 18 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | Calculation |  |  | 0.6525 |  | 0.85125 | 1.3046 | 1 | 0.85125 | 0.6525 | 0.85125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | Calculation |  |  | 0.6525 |  | 1.4325 | 2.1954 | 1.5 | 2.1488 | 0.6525 | 1.4325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 1.9575 | 3 | 1 | 1.9575 | 0.6525 | 1.9575
[10 empty] | Total | 4.9575 | 1.9575 | 4.2413
| 3 | total customers
| 26280 | total (customers*8760)
| 1.9575 | total F
| 0.6525 | SAIFI=total F/total customers
| 1.4138 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016139 | ASUI=1-ASAI
| 4957.5 | ENS=total ENS*1000
| 1652.5 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1451.25
0.15 | 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 5805
0.15 |  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | C | 3870
0.15 |  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | D | 1773.75
0.15 |  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375 | [5 empty] | E | 1451.25
0.15 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4267.5
0.15 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | Calculation |  |  | 0.435 |  | 0.49875 | 1.1466 | 1 | 0.49875 | 0.435 | 0.49875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 0.52125 | 1.178 | 1 | 0.52125 | 0.4425 | 0.52125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.4125 |  | 0.43125 | 1.0455 | 1 | 0.43125 | 0.4125 | 0.43125
[10 empty] | Total | 1.4512 | 1.29 | 1.4512
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.48375 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.5223e-05 | ASUI=1-ASAI
| 1451.25 | ENS=total ENS*1000
| 483.75 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
[10 empty] | Total | 5.805 | 1.935 | 5.805
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 1.935 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99978 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022089 | ASUI=1-ASAI
| 5805 | ENS=total ENS*1000
| 1935 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1 | 1.305 | 0.435 | 1.305
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 1.3275 | 3 | 1 | 1.3275 | 0.4425 | 1.3275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.4125 |  | 1.2375 | 3 | 1 | 1.2375 | 0.4125 | 1.2375
[10 empty] | Total | 3.87 | 1.29 | 3.87
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 1.29 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014726 | ASUI=1-ASAI
| 3870 | ENS=total ENS*1000
| 1290 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 49 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.60375 | 0.93605 | 1 | 0.60375 | 0.645 | 0.60375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.6225 | 0.96512 | 1 | 0.6225 | 0.645 | 0.6225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 47 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 0.5475 | 0.84884 | 1 | 0.5475 | 0.645 | 0.5475
[10 empty] | Total | 1.7738 | 1.935 | 1.7738
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 0.59125 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.7494e-05 | ASUI=1-ASAI
| 1773.75 | ENS=total ENS*1000
| 591.25 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 49 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.90375 | 1.4012 | 1 | 0.90375 | 0.645 | 0.90375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 1.4287 | 2.2151 | 1 | 1.4287 | 0.645 | 1.4287
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
[10 empty] | Total | 4.2675 | 1.935 | 4.2675
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 1.4225 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016239 | ASUI=1-ASAI
| 4267.5 | ENS=total ENS*1000
| 1422.5 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1629.375
0.15 | 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 6772.5
0.15 |  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 4713.75
0.15 |  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 1972.5
0.15 |  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27 | [5 empty] | E | 1629.375
0.15 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5141.25
0.15 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | Calculation |  |  | 0.4425 |  | 0.44625 | 1.0085 | 1 | 0.44625 | 0.4425 | 0.44625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.465 |  | 0.51375 | 1.1048 | 1 | 0.51375 | 0.465 | 0.51375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.4425 |  | 0.44625 | 1.0085 | 1.5 | 0.66938 | 0.4425 | 0.44625
[10 empty] | Total | 1.6294 | 1.35 | 1.4062
| 3 | total customers
| 26280 | total (customers*8760)
| 1.35 | total F
| 0.45 | SAIFI=total F/total customers
| 0.46875 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.351e-05 | ASUI=1-ASAI
| 1629.375 | ENS=total ENS*1000
| 543.125 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1.5 | 2.9025 | 0.645 | 1.935
[10 empty] | Total | 6.7725 | 1.935 | 5.805
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 1.935 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99978 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022089 | ASUI=1-ASAI
| 6772.5 | ENS=total ENS*1000
| 2257.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 1.3275 | 3 | 1 | 1.3275 | 0.4425 | 1.3275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.465 |  | 1.395 | 3 | 1 | 1.395 | 0.465 | 1.395
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.4425 |  | 1.3275 | 3 | 1.5 | 1.9913 | 0.4425 | 1.3275
[10 empty] | Total | 4.7138 | 1.35 | 4.05
| 3 | total customers
| 26280 | total (customers*8760)
| 1.35 | total F
| 0.45 | SAIFI=total F/total customers
| 1.35 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015411 | ASUI=1-ASAI
| 4713.75 | ENS=total ENS*1000
| 1571.25 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 55 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.5475 | 0.84884 | 1 | 0.5475 | 0.645 | 0.5475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.60375 | 0.93605 | 1 | 0.60375 | 0.645 | 0.60375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 0.5475 | 0.84884 | 1.5 | 0.82125 | 0.645 | 0.5475
[10 empty] | Total | 1.9725 | 1.935 | 1.6987
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 0.56625 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.464e-05 | ASUI=1-ASAI
| 1972.5 | ENS=total ENS*1000
| 657.5 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 55 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.82875 | 1.2849 | 1 | 0.82875 | 0.645 | 0.82875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 1.41 | 2.186 | 1 | 1.41 | 0.645 | 1.41
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1.5 | 2.9025 | 0.645 | 1.935
[10 empty] | Total | 5.1412 | 1.935 | 4.1738
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 1.3913 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015882 | ASUI=1-ASAI
| 5141.25 | ENS=total ENS*1000
| 1713.75 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 2 | 1713.8 |  | 6851.3 |  | 4601.3 |  | 2088.8 |  | 1713.8 |  | 4957.5
Feeder 5 | 1451.25 |  | 5805 |  | 3870 |  | 1773.75 |  | 1451.25 |  | 4267.5
Feeder 6 | 1629.375 |  | 6772.5 |  | 4713.75 |  | 1972.5 |  | 1629.375 |  | 5141.25
TOTAL | 4794.425 |  | 19428.8 |  | 13185.05 |  | 5835.05 |  | 4794.425 |  | 14366.25
Analytic | 4.7944 |  | 19.4288 |  | 13.185 |  | 5.835 |  | 4.7944 |  | 14.3663
Monte Carlo_Code | 4.7863 |  | 19.4245 |  | 13.1814 |  | 5.7749 |  | 4.7335 |  | 14.2925
Deviation | 0.16947 |  | 0.022132 |  | 0.027683 |  | 1.0308 |  | 1.2707 |  | 0.51336
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 4.7855 | 4.7848 | 4.7569 | 4.7863 |  | 945000 | 19.438 | 19.4245 | 19.4913 | 19.4819
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 13.1814 | 13.1903 | 13.203 | 13.2231 |  | 47500 | 5.7749 | 5.8423 | 5.7386 | 5.8407
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 4.7646 | 4.7335 | 4.8033 | 4.7959 |  | 1140000 | 14.377 | 14.3727 | 14.2925 | 14.362