## F1_(1-7)
CASE A
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 1.584 | 2.0102 | 0.545 | 0.86328 | 173.36 | 348.48
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.812 |  | 1.656 | 2.0394 | 0.545 | 0.90252 | 178.64 | 364.32
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 1.584 | 2.0102 | 0.545 | 0.86328 | 173.36 | 348.48
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 1.68 | 1.7872 | 0.545 | 0.9156 | 206.8 | 369.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 1.656 | 1.7617 | 0.5 | 0.828 | 188 | 331.2
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 1.68 | 1.7872 | 0.415 | 0.6972 | 9.4 | 16.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 1.656 | 1.7617 | 0.415 | 0.68724 | 9.4 | 16.56
[9 empty] | Total | 5.7571 | 938.96 | 1795.44
1100 | total customers
9636000 | total (customers*8760)
938.96 | total F
0.8536 | SAIFI=total F/total customers
1.6322 | SAIDI=total G/total customers
1.9122 | CAIDI=SAIDI/SAIFI
0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00018633 | ASUI=1-ASAI
5757.12 | ENS=total ENS*1000
5.2337 | AENS=ENS/total customers
CASE B
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.545 | 6.104 | 462 | 2464
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.545 | 6.104 | 462 | 2464
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.545 | 6.104 | 462 | 2464
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.545 | 6.104 | 462 | 2464
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.5 | 5.6 | 420 | 2240
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.415 | 4.648 | 21 | 112
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.415 | 4.648 | 21 | 112
[9 empty] | Total | 39.312 | 2310 | 12320
1100 | total customers
9636000 | total (customers*8760)
2310 | total F
2.1 | SAIFI=total F/total customers
11.2 | SAIDI=total G/total customers
5.3333 | CAIDI=SAIDI/SAIFI
0.99872 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.0012785 | ASUI=1-ASAI
39312 | ENS=total ENS*1000
35.7382 | AENS=ENS/total customers
CASE C
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 3.064 | 3.8883 | 0.545 | 1.6699 | 173.36 | 674.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0 | 0 | 3 | 0
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.812 |  | 3.136 | 3.8621 | 0.545 | 1.7091 | 178.64 | 689.92
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 3.064 | 3.8883 | 0.545 | 1.6699 | 173.36 | 674.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 3.16 | 3.3617 | 0.545 | 1.7222 | 206.8 | 695.2
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 3.136 | 3.3362 | 0.5 | 1.568 | 188 | 627.2
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 3.16 | 3.3617 | 0.415 | 1.3114 | 9.4 | 31.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 3.136 | 3.3362 | 0.415 | 1.3014 | 9.4 | 31.36
[9 empty] | Total | 10.9519 | 938.96 | 3423.44
1100 | total customers
9636000 | total (customers*8760)
938.96 | total F
0.8536 | SAIFI=total F/total customers
3.1122 | SAIDI=total G/total customers
3.646 | CAIDI=SAIDI/SAIFI
0.99964 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00035528 | ASUI=1-ASAI
10951.92 | ENS=total ENS*1000
9.9563 | AENS=ENS/total customers
CASE D
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 2.24 | 1.0667 | 0.545 | 1.2208 | 462 | 492.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 2.3 | 1.0952 | 0.545 | 1.2535 | 462 | 506
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 2.24 | 1.0667 | 0.545 | 1.2208 | 462 | 492.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 3.57 | 1.7 | 0.545 | 1.9456 | 462 | 785.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 3.57 | 1.7 | 0.5 | 1.785 | 420 | 714
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 3.57 | 1.7 | 0.415 | 1.4815 | 21 | 35.7
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 3.57 | 1.7 | 0.415 | 1.4815 | 21 | 35.7
[9 empty] | Total | 10.3888 | 2310 | 3062.4
1100 | total customers
9636000 | total (customers*8760)
2310 | total F
2.1 | SAIFI=total F/total customers
2.784 | SAIDI=total G/total customers
1.3257 | CAIDI=SAIDI/SAIFI
0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00031781 | ASUI=1-ASAI
10388.85 | ENS=total ENS*1000
9.4444 | AENS=ENS/total customers
CASE E
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 1.584 | 2.0102 | 0.545 | 0.86328 | 173.36 | 348.48
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.812 |  | 1.656 | 2.0394 | 0.545 | 0.90252 | 178.64 | 364.32
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 1.584 | 2.0102 | 0.545 | 0.86328 | 173.36 | 348.48
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 1.68 | 1.7872 | 0.545 | 0.9156 | 206.8 | 369.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 1.656 | 1.7617 | 0.5 | 0.828 | 188 | 331.2
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 1.68 | 1.7872 | 0.415 | 0.6972 | 9.4 | 16.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.94 |  | 1.656 | 1.7617 | 0.415 | 0.68724 | 9.4 | 16.56
[9 empty] | Total | 5.7571 | 938.96 | 1795.44
1100 | total customers
9636000 | total (customers*8760)
938.96 | total F
0.8536 | SAIFI=total F/total customers
1.6322 | SAIDI=total G/total customers
1.9122 | CAIDI=SAIDI/SAIFI
0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00018633 | ASUI=1-ASAI
5757.12 | ENS=total ENS*1000
5.2337 | AENS=ENS/total customers
CASE F
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 2.54 | 1.2095 | 0.545 | 1.3843 | 462 | 558.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 4.11 | 1.9571 | 0.545 | 2.2399 | 462 | 904.2
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 5.62 | 2.6762 | 0.545 | 3.0629 | 462 | 1236.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 8.44 | 4.019 | 0.545 | 4.5998 | 462 | 1856.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.1 |  | 8.44 | 4.019 | 0.5 | 4.22 | 420 | 1688
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.415 | 4.648 | 21 | 112
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.1 |  | 11.2 | 5.3333 | 0.415 | 4.648 | 21 | 112
[9 empty] | Total | 24.8029 | 2310 | 6468.2
1100 | total customers
9636000 | total (customers*8760)
2310 | total F
2.1 | SAIFI=total F/total customers
5.8802 | SAIDI=total G/total customers
2.8001 | CAIDI=SAIDI/SAIFI
0.99933 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00067125 | ASUI=1-ASAI
24802.95 | ENS=total ENS*1000
22.5481 | AENS=ENS/total customers

## F2_(8-10)
CASE A & E
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.448 |  | 0.464 | 1.0357 | 1 | 0.464 | 0.448 | 0.464
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.472 |  | 0.536 | 1.1356 | 1.5 | 0.804 | 0.472 | 0.536
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | Calculation |  |  | 0.48 |  | 0.56 | 1.1667 | 1 | 0.56 | 0.48 | 0.56
[9 empty] | Total | 1.828 | 1.4 | 1.56
3 | total customers
26280 | total (customers*8760)
1.4 | total F
0.46667 | SAIFI=total F/total customers
0.52 | SAIDI=total G/total customers
1.1143 | CAIDI=SAIDI/SAIFI
0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
5.9361e-05 | ASUI=1-ASAI
1828 | ENS=total ENS*1000
609.3333 | AENS=ENS/total customers
CASE B
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1.5 | 3.132 | 0.696 | 2.088
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[9 empty] | Total | 7.308 | 2.088 | 6.264
3 | total customers
26280 | total (customers*8760)
2.088 | total F
0.696 | SAIFI=total F/total customers
2.088 | SAIDI=total G/total customers
3 | CAIDI=SAIDI/SAIFI
0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00023836 | ASUI=1-ASAI
7308 | ENS=total ENS*1000
2436 | AENS=ENS/total customers
CASE C
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.448 |  | 1.344 | 3 | 1 | 1.344 | 0.448 | 1.344
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | Calculation |  |  | 0.48 |  | 1.44 | 3 | 1 | 1.44 | 0.48 | 1.44
[9 empty] | Total | 4.908 | 1.4 | 4.2
3 | total customers
26280 | total (customers*8760)
1.4 | total F
0.46667 | SAIFI=total F/total customers
1.4 | SAIDI=total G/total customers
3 | CAIDI=SAIDI/SAIFI
0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00015982 | ASUI=1-ASAI
4908 | ENS=total ENS*1000
1636 | AENS=ENS/total customers
CASE D
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | Calculation |  |  | 0.696 |  | 0.588 | 0.84483 | 1 | 0.588 | 0.696 | 0.588
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | Calculation |  |  | 0.696 |  | 0.648 | 0.93103 | 1.5 | 0.972 | 0.696 | 0.648
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | Calculation |  |  | 0.696 |  | 0.668 | 0.95977 | 1 | 0.668 | 0.696 | 0.668
[9 empty] | Total | 2.228 | 2.088 | 1.904
3 | total customers
26280 | total (customers*8760)
2.088 | total F
0.696 | SAIFI=total F/total customers
0.63467 | SAIDI=total G/total customers
0.91188 | CAIDI=SAIDI/SAIFI
0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
7.2451e-05 | ASUI=1-ASAI
2228 | ENS=total ENS*1000
742.6667 | AENS=ENS/total customers
CASE F
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | Calculation |  |  | 0.696 |  | 0.908 | 1.3046 | 1 | 0.908 | 0.696 | 0.908
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | Calculation |  |  | 0.696 |  | 1.528 | 2.1954 | 1.5 | 2.292 | 0.696 | 1.528
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[9 empty] | Total | 5.288 | 2.088 | 4.524
3 | total customers
26280 | total (customers*8760)
2.088 | total F
0.696 | SAIFI=total F/total customers
1.508 | SAIDI=total G/total customers
2.1667 | CAIDI=SAIDI/SAIFI
0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00017215 | ASUI=1-ASAI
5288 | ENS=total ENS*1000
1762.6667 | AENS=ENS/total customers

## F3_(11-17)
CASE A
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.796 |  | 1.668 | 2.0955 | 0.545 | 0.90906 | 175.12 | 366.96
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 1.644 | 2.0863 | 0.545 | 0.89598 | 173.36 | 361.68
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 1.644 | 2.0863 | 0.545 | 0.89598 | 173.36 | 361.68
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 1.572 | 1.7783 | 0.5 | 0.786 | 176.8 | 314.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 1.644 | 1.8597 | 0.5 | 0.822 | 176.8 | 328.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 1.644 | 1.8597 | 0.415 | 0.68226 | 8.84 | 16.44
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 1.572 | 1.7783 | 0.415 | 0.65238 | 8.84 | 15.72
[9 empty] | Total | 5.6437 | 893.12 | 1765.68
1080 | total customers
9460800 | total (customers*8760)
893.12 | total F
0.82696 | SAIFI=total F/total customers
1.6349 | SAIDI=total G/total customers
1.977 | CAIDI=SAIDI/SAIFI
0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00018663 | ASUI=1-ASAI
5643.66 | ENS=total ENS*1000
5.2256 | AENS=ENS/total customers
CASE B
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.545 | 6.0517 | 454.96 | 2442.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.545 | 6.0517 | 454.96 | 2442.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.545 | 6.0517 | 454.96 | 2442.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.5 | 5.552 | 413.6 | 2220.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.5 | 5.552 | 413.6 | 2220.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.415 | 4.6082 | 20.68 | 111.04
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.415 | 4.6082 | 20.68 | 111.04
[9 empty] | Total | 38.4754 | 2233.44 | 11992.32
1080 | total customers
9460800 | total (customers*8760)
2233.44 | total F
2.068 | SAIFI=total F/total customers
11.104 | SAIDI=total G/total customers
5.3694 | CAIDI=SAIDI/SAIFI
0.99873 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.0012676 | ASUI=1-ASAI
38475.36 | ENS=total ENS*1000
35.6253 | AENS=ENS/total customers
CASE C
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0 | 0 | 3 | 0
|  | 24 | 0.75 | 0 | 0 | 3 | 0
|  | 25 | 0.6 | 0 | 0 | 3 | 0
|  | 27 | 0.75 | 0 | 0 | 3 | 0
|  | 29 | 0.75 | 0 | 0 | 3 | 0
|  | 30 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.796 |  | 3.088 | 3.8794 | 0.545 | 1.683 | 175.12 | 679.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0 | 0 | 3 | 0
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0 | 0 | 3 | 0
|  | 25 | 0.6 | 0 | 0 | 3 | 0
|  | 27 | 0.75 | 0 | 0 | 3 | 0
|  | 29 | 0.75 | 0 | 0 | 3 | 0
|  | 30 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 3.064 | 3.8883 | 0.545 | 1.6699 | 173.36 | 674.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0 | 0 | 3 | 0
|  | 22 | 0.75 | 0 | 0 | 3 | 0
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0 | 0 | 3 | 0
|  | 27 | 0.75 | 0 | 0 | 3 | 0
|  | 29 | 0.75 | 0 | 0 | 3 | 0
|  | 30 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 3.064 | 3.8883 | 0.545 | 1.6699 | 173.36 | 674.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0 | 0 | 3 | 0
|  | 22 | 0.75 | 0 | 0 | 3 | 0
|  | 24 | 0.75 | 0 | 0 | 3 | 0
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0 | 0 | 3 | 0
|  | 30 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 3.352 | 3.7919 | 0.5 | 1.676 | 176.8 | 670.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0 | 0 | 3 | 0
|  | 22 | 0.75 | 0 | 0 | 3 | 0
|  | 24 | 0.75 | 0 | 0 | 3 | 0
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0 | 0 | 3 | 0
|  | 30 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 3.352 | 3.7919 | 0.5 | 1.676 | 176.8 | 670.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0 | 0 | 3 | 0
|  | 22 | 0.75 | 0 | 0 | 3 | 0
|  | 24 | 0.75 | 0 | 0 | 3 | 0
|  | 25 | 0.6 | 0 | 0 | 3 | 0
|  | 27 | 0.75 | 0 | 0 | 3 | 0
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 3.352 | 3.7919 | 0.415 | 1.3911 | 8.84 | 33.52
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0 | 0 | 3 | 0
|  | 22 | 0.75 | 0 | 0 | 3 | 0
|  | 24 | 0.75 | 0 | 0 | 3 | 0
|  | 25 | 0.6 | 0 | 0 | 3 | 0
|  | 27 | 0.75 | 0 | 0 | 3 | 0
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 3.352 | 3.7919 | 0.415 | 1.3911 | 8.84 | 33.52
[9 empty] | Total | 11.1569 | 893.12 | 3435.36
1080 | total customers
9460800 | total (customers*8760)
893.12 | total F
0.82696 | SAIFI=total F/total customers
3.1809 | SAIDI=total G/total customers
3.8465 | CAIDI=SAIDI/SAIFI
0.99964 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00036312 | ASUI=1-ASAI
11156.88 | ENS=total ENS*1000
10.3304 | AENS=ENS/total customers
CASE D
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 2.304 | 1.1141 | 0.545 | 1.2557 | 454.96 | 506.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 2.284 | 1.1044 | 0.545 | 1.2448 | 454.96 | 502.48
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 3.474 | 1.6799 | 0.545 | 1.8933 | 454.96 | 764.28
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 3.474 | 1.6799 | 0.5 | 1.737 | 413.6 | 694.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 2.284 | 1.1044 | 0.5 | 1.142 | 413.6 | 456.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 3.474 | 1.6799 | 0.415 | 1.4417 | 20.68 | 34.74
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 3.474 | 1.6799 | 0.415 | 1.4417 | 20.68 | 34.74
[9 empty] | Total | 10.1562 | 2233.44 | 2994.72
1080 | total customers
9460800 | total (customers*8760)
2233.44 | total F
2.068 | SAIFI=total F/total customers
2.7729 | SAIDI=total G/total customers
1.3409 | CAIDI=SAIDI/SAIFI
0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00031654 | ASUI=1-ASAI
10156.21 | ENS=total ENS*1000
9.4039 | AENS=ENS/total customers
CASE E
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.796 |  | 1.668 | 2.0955 | 0.545 | 0.90906 | 175.12 | 366.96
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 1.644 | 2.0863 | 0.545 | 0.89598 | 173.36 | 361.68
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.788 |  | 1.644 | 2.0863 | 0.545 | 0.89598 | 173.36 | 361.68
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 1.572 | 1.7783 | 0.5 | 0.786 | 176.8 | 314.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 1.644 | 1.8597 | 0.5 | 0.822 | 176.8 | 328.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 1.644 | 1.8597 | 0.415 | 0.68226 | 8.84 | 16.44
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.884 |  | 1.572 | 1.7783 | 0.415 | 0.65238 | 8.84 | 15.72
[9 empty] | Total | 5.6437 | 893.12 | 1765.68
1080 | total customers
9460800 | total (customers*8760)
893.12 | total F
0.82696 | SAIFI=total F/total customers
1.6349 | SAIDI=total G/total customers
1.977 | CAIDI=SAIDI/SAIFI
0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00018663 | ASUI=1-ASAI
5643.66 | ENS=total ENS*1000
5.2256 | AENS=ENS/total customers
CASE F
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 2.604 | 1.2592 | 0.545 | 1.4192 | 454.96 | 572.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 4.094 | 1.9797 | 0.545 | 2.2312 | 454.96 | 900.68
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 6.854 | 3.3143 | 0.545 | 3.7354 | 454.96 | 1507.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.068 |  | 6.854 | 3.3143 | 0.5 | 3.427 | 413.6 | 1370.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 10.324 | 4.9923 | 0.5 | 5.162 | 413.6 | 2064.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.415 | 4.6082 | 20.68 | 111.04
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.068 |  | 11.104 | 5.3694 | 0.415 | 4.6082 | 20.68 | 111.04
[9 empty] | Total | 25.1912 | 2233.44 | 6639.12
1080 | total customers
9460800 | total (customers*8760)
2233.44 | total F
2.068 | SAIFI=total F/total customers
6.1473 | SAIDI=total G/total customers
2.9726 | CAIDI=SAIDI/SAIFI
0.9993 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00070175 | ASUI=1-ASAI
25191.16 | ENS=total ENS*1000
23.3251 | AENS=ENS/total customers

## F4_(18-25)
CASE A
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.545 | 0.90688 | 182.16 | 366.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.592 | 1.9801 | 0.545 | 0.86764 | 176.88 | 350.24
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.545 | 0.90688 | 182.16 | 366.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.545 | 0.90688 | 182.16 | 366.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.592 | 1.9801 | 0.5 | 0.796 | 160.8 | 318.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.5 | 0.832 | 165.6 | 332.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.415 | 0.69056 | 8.28 | 16.64
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.592 | 1.9801 | 0.415 | 0.66068 | 8.04 | 15.92
[9 empty] | Total | 6.5675 | 1066.08 | 2132.24
1300 | total customers
11388000 | total (customers*8760)
1066.08 | total F
0.82006 | SAIFI=total F/total customers
1.6402 | SAIDI=total G/total customers
2.0001 | CAIDI=SAIDI/SAIFI
0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00018724 | ASUI=1-ASAI
6567.52 | ENS=total ENS*1000
5.0519 | AENS=ENS/total customers
CASE B
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.545 | 6.806 | 505.12 | 2747.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.545 | 6.806 | 505.12 | 2747.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.545 | 6.806 | 505.12 | 2747.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.545 | 6.806 | 505.12 | 2747.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.5 | 6.244 | 459.2 | 2497.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.5 | 6.244 | 459.2 | 2497.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.415 | 5.1825 | 22.96 | 124.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.415 | 5.1825 | 22.96 | 124.88
[9 empty] | Total | 50.0769 | 2984.8 | 16234.4
1300 | total customers
11388000 | total (customers*8760)
2984.8 | total F
2.296 | SAIFI=total F/total customers
12.488 | SAIDI=total G/total customers
5.439 | CAIDI=SAIDI/SAIFI
0.99857 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.0014256 | ASUI=1-ASAI
50076.88 | ENS=total ENS*1000
38.5207 | AENS=ENS/total customers
CASE C
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 3.184 | 3.8454 | 0.545 | 1.7353 | 182.16 | 700.48
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0 | 0 | 3 | 0
|  | 37 | 0.75 | 0 | 0 | 3 | 0
|  | 38 | 0.6 | 0 | 0 | 3 | 0
|  | 40 | 0.75 | 0 | 0 | 3 | 0
|  | 42 | 0.75 | 0 | 0 | 3 | 0
|  | 43 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 3.112 | 3.8706 | 0.545 | 1.696 | 176.88 | 684.64
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 3 | 0
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0 | 0 | 3 | 0
|  | 38 | 0.6 | 0 | 0 | 3 | 0
|  | 40 | 0.75 | 0 | 0 | 3 | 0
|  | 42 | 0.75 | 0 | 0 | 3 | 0
|  | 43 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 3.184 | 3.8454 | 0.545 | 1.7353 | 182.16 | 700.48
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 3.184 | 3.8454 | 0.545 | 1.7353 | 182.16 | 700.48
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 3
|  | 35 | 0.75 | 0 | 0 | 3 | 0
|  | 37 | 0.75 | 0 | 0 | 3 | 0
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0 | 0 | 3 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 3.112 | 3.8706 | 0.5 | 1.556 | 160.8 | 622.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 3.184 | 3.8454 | 0.5 | 1.592 | 165.6 | 636.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 3 | 0
|  | 35 | 0.75 | 0 | 0 | 3 | 0
|  | 37 | 0.75 | 0 | 0 | 3 | 0
|  | 38 | 0.6 | 0 | 0 | 3 | 0
|  | 40 | 0.75 | 0 | 0 | 3 | 0
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 3.184 | 3.8454 | 0.415 | 1.3214 | 8.28 | 31.84
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 3 | 0
|  | 35 | 0.75 | 0 | 0 | 3 | 0
|  | 37 | 0.75 | 0 | 0 | 3 | 0
|  | 38 | 0.6 | 0 | 0 | 3 | 0
|  | 40 | 0.75 | 0 | 0 | 3 | 0
|  | 42 | 0.75 | 0 | 0 | 3 | 0
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 3.112 | 3.8706 | 0.415 | 1.2915 | 8.04 | 31.12
[9 empty] | Total | 12.6627 | 1066.08 | 4108.24
1300 | total customers
11388000 | total (customers*8760)
1066.08 | total F
0.82006 | SAIFI=total F/total customers
3.1602 | SAIDI=total G/total customers
3.8536 | CAIDI=SAIDI/SAIFI
0.99964 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00036075 | ASUI=1-ASAI
12662.72 | ENS=total ENS*1000
9.7406 | AENS=ENS/total customers
CASE D
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 2.398 | 1.0444 | 0.545 | 1.3069 | 505.12 | 527.56
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 3.588 | 1.5627 | 0.545 | 1.9555 | 505.12 | 789.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 3.588 | 1.5627 | 0.545 | 1.9555 | 505.12 | 789.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 3.588 | 1.5627 | 0.545 | 1.9555 | 505.12 | 789.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 3.588 | 1.5627 | 0.5 | 1.794 | 459.2 | 717.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 2.398 | 1.0444 | 0.5 | 1.199 | 459.2 | 479.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 3.588 | 1.5627 | 0.415 | 1.489 | 22.96 | 35.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 3.588 | 1.5627 | 0.415 | 1.489 | 22.96 | 35.88
[9 empty] | Total | 13.1443 | 2984.8 | 4164.6
1300 | total customers
11388000 | total (customers*8760)
2984.8 | total F
2.296 | SAIFI=total F/total customers
3.2035 | SAIDI=total G/total customers
1.3953 | CAIDI=SAIDI/SAIFI
0.99963 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.0003657 | ASUI=1-ASAI
13144.33 | ENS=total ENS*1000
10.111 | AENS=ENS/total customers
CASE E
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.545 | 0.90688 | 182.16 | 366.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.592 | 1.9801 | 0.545 | 0.86764 | 176.88 | 350.24
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.545 | 0.90688 | 182.16 | 366.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.545 | 0.90688 | 182.16 | 366.08
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.592 | 1.9801 | 0.5 | 0.796 | 160.8 | 318.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.5 | 0.832 | 165.6 | 332.8
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.828 |  | 1.664 | 2.0097 | 0.415 | 0.69056 | 8.28 | 16.64
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0 | 0 | 3 | 0
|  | 34 | 0.6 | 0 | 0 | 0.5
|  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.592 | 1.9801 | 0.415 | 0.66068 | 8.04 | 15.92
[9 empty] | Total | 6.5675 | 1066.08 | 2132.24
1300 | total customers
11388000 | total (customers*8760)
1066.08 | total F
0.82006 | SAIFI=total F/total customers
1.6402 | SAIDI=total G/total customers
2.0001 | CAIDI=SAIDI/SAIFI
0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00018724 | ASUI=1-ASAI
6567.52 | ENS=total ENS*1000
5.0519 | AENS=ENS/total customers
CASE F
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 2.718 | 1.1838 | 0.545 | 1.4813 | 505.12 | 597.96
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 5.478 | 2.3859 | 0.545 | 2.9855 | 505.12 | 1205.16
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 5.478 | 2.3859 | 0.545 | 2.9855 | 505.12 | 1205.16
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 8.238 | 3.588 | 0.545 | 4.4897 | 505.12 | 1812.36
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 8.238 | 3.588 | 0.5 | 4.119 | 459.2 | 1647.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.296 |  | 9.808 | 4.2718 | 0.5 | 4.904 | 459.2 | 1961.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.415 | 5.1825 | 22.96 | 124.88
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.296 |  | 12.488 | 5.439 | 0.415 | 5.1825 | 22.96 | 124.88
[9 empty] | Total | 31.3301 | 2984.8 | 8679.6
1300 | total customers
11388000 | total (customers*8760)
2984.8 | total F
2.296 | SAIFI=total F/total customers
6.6766 | SAIDI=total G/total customers
2.9079 | CAIDI=SAIDI/SAIFI
0.99924 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00076217 | ASUI=1-ASAI
31330.08 | ENS=total ENS*1000
24.1001 | AENS=ENS/total customers

## F5_(26-28)
CASE A & E
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.464 |  | 0.532 | 1.1466 | 1 | 0.532 | 0.464 | 0.532
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.472 |  | 0.556 | 1.178 | 1 | 0.556 | 0.472 | 0.556
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.44 |  | 0.46 | 1.0455 | 1 | 0.46 | 0.44 | 0.46
[9 empty] | Total | 1.548 | 1.376 | 1.548
3 | total customers
26280 | total (customers*8760)
1.376 | total F
0.45867 | SAIFI=total F/total customers
0.516 | SAIDI=total G/total customers
1.125 | CAIDI=SAIDI/SAIFI
0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
5.8904e-05 | ASUI=1-ASAI
1548 | ENS=total ENS*1000
516 | AENS=ENS/total customers
CASE B
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[9 empty] | Total | 6.192 | 2.064 | 6.192
3 | total customers
26280 | total (customers*8760)
2.064 | total F
0.688 | SAIFI=total F/total customers
2.064 | SAIDI=total G/total customers
3 | CAIDI=SAIDI/SAIFI
0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00023562 | ASUI=1-ASAI
6192 | ENS=total ENS*1000
2064 | AENS=ENS/total customers
CASE C
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.464 |  | 1.392 | 3 | 1 | 1.392 | 0.464 | 1.392
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.44 |  | 1.32 | 3 | 1 | 1.32 | 0.44 | 1.32
[9 empty] | Total | 4.128 | 1.376 | 4.128
3 | total customers
26280 | total (customers*8760)
1.376 | total F
0.45867 | SAIFI=total F/total customers
1.376 | SAIDI=total G/total customers
3 | CAIDI=SAIDI/SAIFI
0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00015708 | ASUI=1-ASAI
4128 | ENS=total ENS*1000
1376 | AENS=ENS/total customers
CASE D
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | Calculation |  |  | 0.688 |  | 0.664 | 0.96512 | 1 | 0.664 | 0.688 | 0.664
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
[9 empty] | Total | 1.892 | 2.064 | 1.892
3 | total customers
26280 | total (customers*8760)
2.064 | total F
0.688 | SAIFI=total F/total customers
0.63067 | SAIDI=total G/total customers
0.91667 | CAIDI=SAIDI/SAIFI
0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
7.1994e-05 | ASUI=1-ASAI
1892 | ENS=total ENS*1000
630.6667 | AENS=ENS/total customers
CASE F
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | Calculation |  |  | 0.688 |  | 0.964 | 1.4012 | 1 | 0.964 | 0.688 | 0.964
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | Calculation |  |  | 0.688 |  | 1.524 | 2.2151 | 1 | 1.524 | 0.688 | 1.524
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[9 empty] | Total | 4.552 | 2.064 | 4.552
3 | total customers
26280 | total (customers*8760)
2.064 | total F
0.688 | SAIFI=total F/total customers
1.5173 | SAIDI=total G/total customers
2.2054 | CAIDI=SAIDI/SAIFI
0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00017321 | ASUI=1-ASAI
4552 | ENS=total ENS*1000
1517.3333 | AENS=ENS/total customers

## F6_(29-31)
CASE A & E
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1 | 0.476 | 0.472 | 0.476
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.496 |  | 0.548 | 1.1048 | 1 | 0.548 | 0.496 | 0.548
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1.5 | 0.714 | 0.472 | 0.476
[9 empty] | Total | 1.738 | 1.44 | 1.5
3 | total customers
26280 | total (customers*8760)
1.44 | total F
0.48 | SAIFI=total F/total customers
0.5 | SAIDI=total G/total customers
1.0417 | CAIDI=SAIDI/SAIFI
0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
5.7078e-05 | ASUI=1-ASAI
1738 | ENS=total ENS*1000
579.3333 | AENS=ENS/total customers
CASE B
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[9 empty] | Total | 7.224 | 2.064 | 6.192
3 | total customers
26280 | total (customers*8760)
2.064 | total F
0.688 | SAIFI=total F/total customers
2.064 | SAIDI=total G/total customers
3 | CAIDI=SAIDI/SAIFI
0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00023562 | ASUI=1-ASAI
7224 | ENS=total ENS*1000
2408 | AENS=ENS/total customers
CASE C
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  | Calculation |  |  | 0.496 |  | 1.488 | 3 | 1 | 1.488 | 0.496 | 1.488
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
[9 empty] | Total | 5.028 | 1.44 | 4.32
3 | total customers
26280 | total (customers*8760)
1.44 | total F
0.48 | SAIFI=total F/total customers
1.44 | SAIDI=total G/total customers
3 | CAIDI=SAIDI/SAIFI
0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00016438 | ASUI=1-ASAI
5028 | ENS=total ENS*1000
1676 | AENS=ENS/total customers
CASE D
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1.5 | 0.876 | 0.688 | 0.584
[9 empty] | Total | 2.104 | 2.064 | 1.812
3 | total customers
26280 | total (customers*8760)
2.064 | total F
0.688 | SAIFI=total F/total customers
0.604 | SAIDI=total G/total customers
0.87791 | CAIDI=SAIDI/SAIFI
0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
6.895e-05 | ASUI=1-ASAI
2104 | ENS=total ENS*1000
701.3333 | AENS=ENS/total customers
CASE F
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | Calculation |  |  | 0.688 |  | 0.884 | 1.2849 | 1 | 0.884 | 0.688 | 0.884
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | Calculation |  |  | 0.688 |  | 1.504 | 2.186 | 1 | 1.504 | 0.688 | 1.504
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[9 empty] | Total | 5.484 | 2.064 | 4.452
3 | total customers
26280 | total (customers*8760)
2.064 | total F
0.688 | SAIFI=total F/total customers
1.484 | SAIDI=total G/total customers
2.157 | CAIDI=SAIDI/SAIFI
0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00016941 | ASUI=1-ASAI
5484 | ENS=total ENS*1000
1828 | AENS=ENS/total customers

## F7_(32-38)
CASE A
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.672 | 2.0796 | 0.545 | 0.91124 | 176.88 | 367.84
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.672 | 2.0796 | 0.545 | 0.91124 | 176.88 | 367.84
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.772 |  | 1.576 | 2.0415 | 0.545 | 0.85892 | 169.84 | 346.72
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 1.672 | 1.8578 | 0.545 | 0.91124 | 198 | 367.84
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 1.576 | 1.7511 | 0.5 | 0.788 | 180 | 315.2
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 1.672 | 1.8578 | 0.5 | 0.836 | 180 | 334.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 1.576 | 1.7511 | 0.415 | 0.65404 | 9 | 15.76
[9 empty] | Total | 5.8707 | 1090.6 | 2115.6
1290 | total customers
11300400 | total (customers*8760)
1090.6 | total F
0.84543 | SAIFI=total F/total customers
1.64 | SAIDI=total G/total customers
1.9398 | CAIDI=SAIDI/SAIFI
0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00018721 | ASUI=1-ASAI
5870.68 | ENS=total ENS*1000
4.5509 | AENS=ENS/total customers
CASE B
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.545 | 6.0648 | 456.72 | 2448.16
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.545 | 6.0648 | 456.72 | 2448.16
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.545 | 6.0648 | 456.72 | 2448.16
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.545 | 6.0648 | 456.72 | 2448.16
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.5 | 5.564 | 415.2 | 2225.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.5 | 5.564 | 415.2 | 2225.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.415 | 4.6181 | 20.76 | 111.28
[9 empty] | Total | 40.0052 | 2678.04 | 14355.12
1290 | total customers
11300400 | total (customers*8760)
2678.04 | total F
2.076 | SAIFI=total F/total customers
11.128 | SAIDI=total G/total customers
5.3603 | CAIDI=SAIDI/SAIFI
0.99873 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.0012703 | ASUI=1-ASAI
40005.16 | ENS=total ENS*1000
31.0118 | AENS=ENS/total customers
CASE C
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0 | 0 | 3 | 0
|  | 61 | 0.6 | 0 | 0 | 3 | 0
|  | 62 | 0.8 | 0 | 0 | 3 | 0
|  | 64 | 0.6 | 0 | 0 | 3 | 0
|  | 66 | 0.8 | 0 | 0 | 3 | 0
|  | 67 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 3.112 | 3.8706 | 0.545 | 1.696 | 176.88 | 684.64
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0 | 0 | 3 | 0
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0 | 0 | 3 | 0
|  | 62 | 0.8 | 0 | 0 | 3 | 0
|  | 64 | 0.6 | 0 | 0 | 3 | 0
|  | 66 | 0.8 | 0 | 0 | 3 | 0
|  | 67 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 3.112 | 3.8706 | 0.545 | 1.696 | 176.88 | 684.64
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0 | 0 | 3 | 0
|  | 59 | 0.8 | 0 | 0 | 3 | 0
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0 | 0 | 3 | 0
|  | 64 | 0.6 | 0 | 0 | 3 | 0
|  | 66 | 0.8 | 0 | 0 | 3 | 0
|  | 67 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.772 |  | 3.016 | 3.9067 | 0.545 | 1.6437 | 169.84 | 663.52
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0 | 0 | 3 | 0
|  | 59 | 0.8 | 0 | 0 | 3 | 0
|  | 61 | 0.6 | 0 | 0 | 3 | 0
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0 | 0 | 3 | 0
|  | 67 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 3.4 | 3.7778 | 0.545 | 1.853 | 198 | 748
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0 | 0 | 3 | 0
|  | 59 | 0.8 | 0 | 0 | 3 | 0
|  | 61 | 0.6 | 0 | 0 | 3 | 0
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0 | 0 | 3 | 0
|  | 67 | 0.6 | 0 | 0 | 3 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 3.4 | 3.7778 | 0.5 | 1.7 | 180 | 680
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0 | 0 | 3 | 0
|  | 59 | 0.8 | 0 | 0 | 3 | 0
|  | 61 | 0.6 | 0 | 0 | 3 | 0
|  | 62 | 0.8 | 0 | 0 | 3 | 0
|  | 64 | 0.6 | 0 | 0 | 3 | 0
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 3.4 | 3.7778 | 0.5 | 1.7 | 180 | 680
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0 | 0 | 3 | 0
|  | 59 | 0.8 | 0 | 0 | 3 | 0
|  | 61 | 0.6 | 0 | 0 | 3 | 0
|  | 62 | 0.8 | 0 | 0 | 3 | 0
|  | 64 | 0.6 | 0 | 0 | 3 | 0
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 3.4 | 3.7778 | 0.415 | 1.411 | 9 | 34
[9 empty] | Total | 11.6998 | 1090.6 | 4174.8
1290 | total customers
11300400 | total (customers*8760)
1090.6 | total F
0.84543 | SAIFI=total F/total customers
3.2363 | SAIDI=total G/total customers
3.828 | CAIDI=SAIDI/SAIFI
0.99963 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00036944 | ASUI=1-ASAI
11699.8 | ENS=total ENS*1000
9.0696 | AENS=ENS/total customers
CASE D
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 2.308 | 1.1118 | 0.545 | 1.2579 | 456.72 | 507.76
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 2.308 | 1.1118 | 0.545 | 1.2579 | 456.72 | 507.76
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 3.498 | 1.685 | 0.545 | 1.9064 | 456.72 | 769.56
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 3.498 | 1.685 | 0.545 | 1.9064 | 456.72 | 769.56
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 2.228 | 1.0732 | 0.5 | 1.114 | 415.2 | 445.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 3.498 | 1.685 | 0.5 | 1.749 | 415.2 | 699.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 3.498 | 1.685 | 0.415 | 1.4517 | 20.76 | 34.98
[9 empty] | Total | 10.6432 | 2678.04 | 3734.82
1290 | total customers
11300400 | total (customers*8760)
2678.04 | total F
2.076 | SAIFI=total F/total customers
2.8952 | SAIDI=total G/total customers
1.3946 | CAIDI=SAIDI/SAIFI
0.99967 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.0003305 | ASUI=1-ASAI
10643.21 | ENS=total ENS*1000
8.2506 | AENS=ENS/total customers
CASE E
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.672 | 2.0796 | 0.545 | 0.91124 | 176.88 | 367.84
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.804 |  | 1.672 | 2.0796 | 0.545 | 0.91124 | 176.88 | 367.84
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.772 |  | 1.576 | 2.0415 | 0.545 | 0.85892 | 169.84 | 346.72
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 1.672 | 1.8578 | 0.545 | 0.91124 | 198 | 367.84
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 1.576 | 1.7511 | 0.5 | 0.788 | 180 | 315.2
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 1.672 | 1.8578 | 0.5 | 0.836 | 180 | 334.4
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | x former |  |  | 0 | 0 | 0
|  | Calculation |  |  | 0.9 |  | 1.576 | 1.7511 | 0.415 | 0.65404 | 9 | 15.76
[9 empty] | Total | 5.8707 | 1090.6 | 2115.6
1290 | total customers
11300400 | total (customers*8760)
1090.6 | total F
0.84543 | SAIFI=total F/total customers
1.64 | SAIDI=total G/total customers
1.9398 | CAIDI=SAIDI/SAIFI
0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00018721 | ASUI=1-ASAI
5870.68 | ENS=total ENS*1000
4.5509 | AENS=ENS/total customers
CASE F
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 2.608 | 1.2563 | 0.545 | 1.4214 | 456.72 | 573.76
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 4.118 | 1.9836 | 0.545 | 2.2443 | 456.72 | 905.96
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 6.878 | 3.3131 | 0.545 | 3.7485 | 456.72 | 1513.16
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 6.878 | 3.3131 | 0.545 | 3.7485 | 456.72 | 1513.16
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | x former |  |  | 0.1 | 0.5 | 0.05
|  | Calculation |  |  | 2.076 |  | 8.368 | 4.0308 | 0.5 | 4.184 | 415.2 | 1673.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.5 | 5.564 | 415.2 | 2225.6
Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | x former |  |  | 0.1 | 10 | 1
|  | Calculation |  |  | 2.076 |  | 11.128 | 5.3603 | 0.415 | 4.6181 | 20.76 | 111.28
[9 empty] | Total | 25.5288 | 2678.04 | 8516.52
1290 | total customers
11300400 | total (customers*8760)
2678.04 | total F
2.076 | SAIFI=total F/total customers
6.602 | SAIDI=total G/total customers
3.1801 | CAIDI=SAIDI/SAIFI
0.99925 | ASAI=total(customers*8760)-total G/total (customers*8760)
0.00075365 | ASUI=1-ASAI
25528.81 | ENS=total ENS*1000
19.7898 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 5757.12 | 1100 | 39312 | 1100 | 10951.92 | 1100 | 10388.85 | 1100 | 5757.12 | 1100 | 24802.95 | 1100
Feeder 2 | 1828 | 3 | 7308 | 3 | 4908 | 3 | 2228 | 3 | 1828 | 3 | 5288 | 3
Feeder 3 | 5643.66 | 1080 | 38475.36 | 1080 | 11156.88 | 1080 | 10156.21 | 1080 | 5643.66 | 1080 | 25191.16 | 1080
Feeder 4 | 6567.52 | 1300 | 50076.88 | 1300 | 12662.72 | 1300 | 13144.33 | 1300 | 6567.52 | 1300 | 31330.08 | 1300
Feeder 5 | 1548 | 3 | 6192 | 3 | 4128 | 3 | 1892 | 3 | 1548 | 3 | 4552 | 3
Feeder 6 | 1738 | 3 | 7224 | 3 | 5028 | 3 | 2104 | 3 | 1738 | 3 | 5484 | 3
Feeder 7 | 5870.68 | 1290 | 40005.16 | 1290 | 11699.8 | 1290 | 10643.21 | 1290 | 5870.68 | 1290 | 25528.81 | 1290
TOTAL | 28952.98 | 4779 | 188593.4 | 4779 | 60535.32 | 4779 | 50556.6 | 4779 | 28952.98 | 4779 | 122177 | 4779
Analytic | 28.953 |  | 188.5934 |  | 60.5353 |  | 50.5566 |  | 28.953 |  | 122.177
Monte Carlo_Code | 28.922 |  | 188.57 |  | 59.383 |  | 50.44 |  | 28.945 |  | 121.18
Deviation | 0.107 |  | 0.012408 |  | 1.9035 |  | 0.23063 |  | 0.027562 |  | 0.81603