## F1_(1-7)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.005 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2422.62
0.005 | 0.16 | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 15970.5
0.005 | 0.16 |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 7617.42
0.005 | 0.16 |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 4361.8125
0.005 | 0.16 |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 2422.62
0.005 | 0.16 |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 10725.6125
0.005 | 0.16 |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
0.005 | 0.16 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | x former |  |  | 0.005 | 10 | 0.05
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | Calculation |  |  | 0.693 |  | 0.634 | 0.91486 | 0.545 | 0.34553 | 152.46 | 139.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.717 |  | 0.706 | 0.98466 | 0.545 | 0.38477 | 157.74 | 155.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 0.634 | 0.91486 | 0.545 | 0.34553 | 152.46 | 139.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 0.73 | 0.86391 | 0.545 | 0.39785 | 185.9 | 160.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 0.706 | 0.8355 | 0.5 | 0.353 | 169 | 141.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 0.73 | 0.86391 | 0.415 | 0.30295 | 8.45 | 7.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 0.706 | 0.8355 | 0.415 | 0.29299 | 8.45 | 7.06
[11 empty] | Total | 2.4226 | 834.46 | 750.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 834.46 | total F
|  | 0.7586 | SAIFI=total F/total customers
|  | 0.68222 | SAIDI=total G/total customers
|  | 0.89931 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 7.7879e-05 | ASUI=1-ASAI
|  | 2422.62 | ENS=total ENS*1000
|  | 2.2024 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.545 | 2.4797 | 315.7 | 1001
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.545 | 2.4797 | 315.7 | 1001
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.545 | 2.4797 | 315.7 | 1001
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.545 | 2.4797 | 315.7 | 1001
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.5 | 2.275 | 287 | 910
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.415 | 1.8882 | 14.35 | 45.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.415 | 1.8882 | 14.35 | 45.5
[11 empty] | Total | 15.9705 | 1578.5 | 5005
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1578.5 | total F
|  | 1.435 | SAIFI=total F/total customers
|  | 4.55 | SAIDI=total G/total customers
|  | 3.1707 | CAIDI=SAIDI/SAIFI
|  | 0.99948 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00051941 | ASUI=1-ASAI
|  | 15970.5 | ENS=total ENS*1000
|  | 14.5186 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 2.114 | 3.0505 | 0.545 | 1.1521 | 152.46 | 465.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.717 |  | 2.186 | 3.0488 | 0.545 | 1.1914 | 157.74 | 480.92
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 2.114 | 3.0505 | 0.545 | 1.1521 | 152.46 | 465.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 2.21 | 2.6154 | 0.545 | 1.2045 | 185.9 | 486.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 2.186 | 2.587 | 0.5 | 1.093 | 169 | 437.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 2.21 | 2.6154 | 0.415 | 0.91715 | 8.45 | 22.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 2.186 | 2.587 | 0.415 | 0.90719 | 8.45 | 21.86
[11 empty] | Total | 7.6174 | 834.46 | 2378.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 834.46 | total F
|  | 0.7586 | SAIFI=total F/total customers
|  | 2.1622 | SAIDI=total G/total customers
|  | 2.8503 | CAIDI=SAIDI/SAIFI
|  | 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00024683 | ASUI=1-ASAI
|  | 7617.42 | ENS=total ENS*1000
|  | 6.9249 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.005 | 0.70035 | 0.545 | 0.54773 | 315.7 | 221.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.065 | 0.74216 | 0.545 | 0.58042 | 315.7 | 234.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.005 | 0.70035 | 0.545 | 0.54773 | 315.7 | 221.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.4325 | 0.99826 | 0.545 | 0.78071 | 315.7 | 315.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.4325 | 0.99826 | 0.5 | 0.71625 | 287 | 286.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.4325 | 0.99826 | 0.415 | 0.59449 | 14.35 | 14.325
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.4325 | 0.99826 | 0.415 | 0.59449 | 14.35 | 14.325
[11 empty] | Total | 4.3618 | 1578.5 | 1306.8
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1578.5 | total F
|  | 1.435 | SAIFI=total F/total customers
|  | 1.188 | SAIDI=total G/total customers
|  | 0.82787 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00013562 | ASUI=1-ASAI
|  | 4361.8125 | ENS=total ENS*1000
|  | 3.9653 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 0.634 | 0.91486 | 0.545 | 0.34553 | 152.46 | 139.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.717 |  | 0.706 | 0.98466 | 0.545 | 0.38477 | 157.74 | 155.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 0.634 | 0.91486 | 0.545 | 0.34553 | 152.46 | 139.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 0.73 | 0.86391 | 0.545 | 0.39785 | 185.9 | 160.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 0.706 | 0.8355 | 0.5 | 0.353 | 169 | 141.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 0.73 | 0.86391 | 0.415 | 0.30295 | 8.45 | 7.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.845 |  | 0.706 | 0.8355 | 0.415 | 0.29299 | 8.45 | 7.06
[11 empty] | Total | 2.4226 | 834.46 | 750.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 834.46 | total F
|  | 0.7586 | SAIFI=total F/total customers
|  | 0.68222 | SAIDI=total G/total customers
|  | 0.89931 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 7.7879e-05 | ASUI=1-ASAI
|  | 2422.62 | ENS=total ENS*1000
|  | 2.2024 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.305 | 0.90941 | 0.545 | 0.71123 | 315.7 | 287.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 1.9725 | 1.3746 | 0.545 | 1.075 | 315.7 | 433.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 2.58 | 1.7979 | 0.545 | 1.4061 | 315.7 | 567.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 3.595 | 2.5052 | 0.545 | 1.9593 | 315.7 | 790.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.435 |  | 3.595 | 2.5052 | 0.5 | 1.7975 | 287 | 719
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.415 | 1.8882 | 14.35 | 45.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.435 |  | 4.55 | 3.1707 | 0.415 | 1.8882 | 14.35 | 45.5
[11 empty] | Total | 10.7256 | 1578.5 | 2889.55
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1578.5 | total F
|  | 1.435 | SAIFI=total F/total customers
|  | 2.6269 | SAIDI=total G/total customers
|  | 1.8306 | CAIDI=SAIDI/SAIFI
|  | 0.9997 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00029987 | ASUI=1-ASAI
|  | 10725.6125 | ENS=total ENS*1000
|  | 9.7506 | AENS=ENS/total customers

## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1828
0.16 | 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 7308
0.16 |  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 4908
0.16 |  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | D | 2228
0.16 |  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1828
0.16 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5288
0.16 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.448 |  | 0.464 | 1.0357 | 1 | 0.464 | 0.448 | 0.464
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.536 | 1.1356 | 1.5 | 0.804 | 0.472 | 0.536
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 0.56 | 1.1667 | 1 | 0.56 | 0.48 | 0.56
[10 empty] | Total | 1.828 | 1.4 | 1.56
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 0.52 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.9361e-05 | ASUI=1-ASAI
| 1828 | ENS=total ENS*1000
| 609.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1.5 | 3.132 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 7.308 | 2.088 | 6.264
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 2.088 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023836 | ASUI=1-ASAI
| 7308 | ENS=total ENS*1000
| 2436 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.448 |  | 1.344 | 3 | 1 | 1.344 | 0.448 | 1.344
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 1.44 | 3 | 1 | 1.44 | 0.48 | 1.44
[10 empty] | Total | 4.908 | 1.4 | 4.2
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 1.4 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015982 | ASUI=1-ASAI
| 4908 | ENS=total ENS*1000
| 1636 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.588 | 0.84483 | 1 | 0.588 | 0.696 | 0.588
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.648 | 0.93103 | 1.5 | 0.972 | 0.696 | 0.648
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 0.668 | 0.95977 | 1 | 0.668 | 0.696 | 0.668
[10 empty] | Total | 2.228 | 2.088 | 1.904
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 0.63467 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.2451e-05 | ASUI=1-ASAI
| 2228 | ENS=total ENS*1000
| 742.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.908 | 1.3046 | 1 | 0.908 | 0.696 | 0.908
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 1.528 | 2.1954 | 1.5 | 2.292 | 0.696 | 1.528
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 5.288 | 2.088 | 4.524
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 1.508 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017215 | ASUI=1-ASAI
| 5288 | ENS=total ENS*1000
| 1762.6667 | AENS=ENS/total customers

## F3_(11-17)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.005 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2351.91
0.005 | 0.16 | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 15433.11
0.005 | 0.16 |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 7865.13
0.005 | 0.16 |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 4184.7475
0.005 | 0.16 |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 2351.91
0.005 | 0.16 |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 10388.735
0.005 | 0.16 |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.005 | 0.16 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | x former |  |  | 0.005 | 10 | 0.05
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | Calculation |  |  | 0.701 |  | 0.718 | 1.0243 | 0.545 | 0.39131 | 154.22 | 157.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 0.694 | 1.0014 | 0.545 | 0.37823 | 152.46 | 152.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 0.694 | 1.0014 | 0.545 | 0.37823 | 152.46 | 152.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 0.622 | 0.78834 | 0.5 | 0.311 | 157.8 | 124.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 0.694 | 0.87959 | 0.5 | 0.347 | 157.8 | 138.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 0.694 | 0.87959 | 0.415 | 0.28801 | 7.89 | 6.94
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 0.622 | 0.78834 | 0.415 | 0.25813 | 7.89 | 6.22
[11 empty] | Total | 2.3519 | 790.52 | 739.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 790.52 | total F
|  | 0.73196 | SAIFI=total F/total customers
|  | 0.68489 | SAIDI=total G/total customers
|  | 0.93569 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 7.8184e-05 | ASUI=1-ASAI
|  | 2351.91 | ENS=total ENS*1000
|  | 2.1777 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.545 | 2.4274 | 308.66 | 979.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.545 | 2.4274 | 308.66 | 979.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.545 | 2.4274 | 308.66 | 979.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.5 | 2.227 | 280.6 | 890.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.5 | 2.227 | 280.6 | 890.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.415 | 1.8484 | 14.03 | 44.54
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.415 | 1.8484 | 14.03 | 44.54
[11 empty] | Total | 15.4331 | 1515.24 | 4810.32
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1515.24 | total F
|  | 1.403 | SAIFI=total F/total customers
|  | 4.454 | SAIDI=total G/total customers
|  | 3.1746 | CAIDI=SAIDI/SAIFI
|  | 0.99949 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00050845 | ASUI=1-ASAI
|  | 15433.11 | ENS=total ENS*1000
|  | 14.2899 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.701 |  | 2.138 | 3.0499 | 0.545 | 1.1652 | 154.22 | 470.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 2.114 | 3.0505 | 0.545 | 1.1521 | 152.46 | 465.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 2.114 | 3.0505 | 0.545 | 1.1521 | 152.46 | 465.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 2.402 | 3.0444 | 0.5 | 1.201 | 157.8 | 480.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 2.402 | 3.0444 | 0.5 | 1.201 | 157.8 | 480.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 2.402 | 3.0444 | 0.415 | 0.99683 | 7.89 | 24.02
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 2.402 | 3.0444 | 0.415 | 0.99683 | 7.89 | 24.02
[11 empty] | Total | 7.8651 | 790.52 | 2409.36
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 790.52 | total F
|  | 0.73196 | SAIFI=total F/total customers
|  | 2.2309 | SAIDI=total G/total customers
|  | 3.0478 | CAIDI=SAIDI/SAIFI
|  | 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00025467 | ASUI=1-ASAI
|  | 7865.13 | ENS=total ENS*1000
|  | 7.2825 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.069 | 0.76194 | 0.545 | 0.58261 | 308.66 | 235.18
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.049 | 0.74768 | 0.545 | 0.57171 | 308.66 | 230.78
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.3365 | 0.9526 | 0.545 | 0.72839 | 308.66 | 294.03
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.3365 | 0.9526 | 0.5 | 0.66825 | 280.6 | 267.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.049 | 0.74768 | 0.5 | 0.5245 | 280.6 | 209.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.3365 | 0.9526 | 0.415 | 0.55465 | 14.03 | 13.365
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.3365 | 0.9526 | 0.415 | 0.55465 | 14.03 | 13.365
[11 empty] | Total | 4.1847 | 1515.24 | 1263.82
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1515.24 | total F
|  | 1.403 | SAIFI=total F/total customers
|  | 1.1702 | SAIDI=total G/total customers
|  | 0.83407 | CAIDI=SAIDI/SAIFI
|  | 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00013358 | ASUI=1-ASAI
|  | 4184.7475 | ENS=total ENS*1000
|  | 3.8748 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.701 |  | 0.718 | 1.0243 | 0.545 | 0.39131 | 154.22 | 157.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 0.694 | 1.0014 | 0.545 | 0.37823 | 152.46 | 152.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.693 |  | 0.694 | 1.0014 | 0.545 | 0.37823 | 152.46 | 152.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 0.622 | 0.78834 | 0.5 | 0.311 | 157.8 | 124.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 0.694 | 0.87959 | 0.5 | 0.347 | 157.8 | 138.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 0.694 | 0.87959 | 0.415 | 0.28801 | 7.89 | 6.94
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.789 |  | 0.622 | 0.78834 | 0.415 | 0.25813 | 7.89 | 6.22
[11 empty] | Total | 2.3519 | 790.52 | 739.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 790.52 | total F
|  | 0.73196 | SAIFI=total F/total customers
|  | 0.68489 | SAIDI=total G/total customers
|  | 0.93569 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 7.8184e-05 | ASUI=1-ASAI
|  | 2351.91 | ENS=total ENS*1000
|  | 2.1777 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.369 | 0.97577 | 0.545 | 0.74611 | 308.66 | 301.18
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 1.9565 | 1.3945 | 0.545 | 1.0663 | 308.66 | 430.43
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 2.9115 | 2.0752 | 0.545 | 1.5868 | 308.66 | 640.53
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.403 |  | 2.9115 | 2.0752 | 0.5 | 1.4557 | 280.6 | 582.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 3.674 | 2.6187 | 0.5 | 1.837 | 280.6 | 734.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.415 | 1.8484 | 14.03 | 44.54
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.403 |  | 4.454 | 3.1746 | 0.415 | 1.8484 | 14.03 | 44.54
[11 empty] | Total | 10.3887 | 1515.24 | 2778.32
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1515.24 | total F
|  | 1.403 | SAIFI=total F/total customers
|  | 2.5725 | SAIDI=total G/total customers
|  | 1.8336 | CAIDI=SAIDI/SAIFI
|  | 0.99971 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00029367 | ASUI=1-ASAI
|  | 10388.735 | ENS=total ENS*1000
|  | 9.6192 | AENS=ENS/total customers

## F4_(18-25)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.005 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2758.02
0.005 | 0.16 | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 19600.88
0.005 | 0.16 |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 8853.22
0.005 | 0.16 |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 5325.5925
0.005 | 0.16 |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 2758.02
0.005 | 0.16 |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 12947.58
0.005 | 0.16 |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
0.005 | 0.16 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | x former |  |  | 0.005 | 10 | 0.05
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.545 | 0.38913 | 161.26 | 157.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.642 | 0.9055 | 0.545 | 0.34989 | 155.98 | 141.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.545 | 0.38913 | 161.26 | 157.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.545 | 0.38913 | 161.26 | 157.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.642 | 0.9055 | 0.5 | 0.321 | 141.8 | 128.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.5 | 0.357 | 146.6 | 142.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.415 | 0.29631 | 7.33 | 7.14
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.642 | 0.9055 | 0.415 | 0.26643 | 7.09 | 6.42
[11 empty] | Total | 2.758 | 942.58 | 897.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 942.58 | total F
|  | 0.72506 | SAIFI=total F/total customers
|  | 0.69018 | SAIDI=total G/total customers
|  | 0.9519 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 7.8788e-05 | ASUI=1-ASAI
|  | 2758.02 | ENS=total ENS*1000
|  | 2.1216 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.545 | 2.664 | 337.92 | 1075.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.545 | 2.664 | 337.92 | 1075.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.545 | 2.664 | 337.92 | 1075.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.545 | 2.664 | 337.92 | 1075.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.5 | 2.444 | 307.2 | 977.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.5 | 2.444 | 307.2 | 977.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.415 | 2.0285 | 15.36 | 48.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.415 | 2.0285 | 15.36 | 48.88
[11 empty] | Total | 19.6009 | 1996.8 | 6354.4
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 1996.8 | total F
|  | 1.536 | SAIFI=total F/total customers
|  | 4.888 | SAIDI=total G/total customers
|  | 3.1823 | CAIDI=SAIDI/SAIFI
|  | 0.99944 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00055799 | ASUI=1-ASAI
|  | 19600.88 | ENS=total ENS*1000
|  | 15.0776 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 2.234 | 3.0477 | 0.545 | 1.2175 | 161.26 | 491.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 2.162 | 3.0494 | 0.545 | 1.1783 | 155.98 | 475.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 2.234 | 3.0477 | 0.545 | 1.2175 | 161.26 | 491.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 2.234 | 3.0477 | 0.545 | 1.2175 | 161.26 | 491.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 2.162 | 3.0494 | 0.5 | 1.081 | 141.8 | 432.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 2.234 | 3.0477 | 0.5 | 1.117 | 146.6 | 446.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 2.234 | 3.0477 | 0.415 | 0.92711 | 7.33 | 22.34
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 2.162 | 3.0494 | 0.415 | 0.89723 | 7.09 | 21.62
[11 empty] | Total | 8.8532 | 942.58 | 2873.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 942.58 | total F
|  | 0.72506 | SAIFI=total F/total customers
|  | 2.2102 | SAIDI=total G/total customers
|  | 3.0483 | CAIDI=SAIDI/SAIFI
|  | 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0002523 | ASUI=1-ASAI
|  | 8853.22 | ENS=total ENS*1000
|  | 6.8102 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.1155 | 0.72624 | 0.545 | 0.60795 | 337.92 | 245.41
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.403 | 0.91341 | 0.545 | 0.76464 | 337.92 | 308.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.403 | 0.91341 | 0.545 | 0.76464 | 337.92 | 308.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.403 | 0.91341 | 0.545 | 0.76464 | 337.92 | 308.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.403 | 0.91341 | 0.5 | 0.7015 | 307.2 | 280.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.1155 | 0.72624 | 0.5 | 0.55775 | 307.2 | 223.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.403 | 0.91341 | 0.415 | 0.58224 | 15.36 | 14.03
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.403 | 0.91341 | 0.415 | 0.58224 | 15.36 | 14.03
[11 empty] | Total | 5.3256 | 1996.8 | 1703.15
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 1996.8 | total F
|  | 1.536 | SAIFI=total F/total customers
|  | 1.3101 | SAIDI=total G/total customers
|  | 0.85294 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014956 | ASUI=1-ASAI
|  | 5325.5925 | ENS=total ENS*1000
|  | 4.0966 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.545 | 0.38913 | 161.26 | 157.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.642 | 0.9055 | 0.545 | 0.34989 | 155.98 | 141.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.545 | 0.38913 | 161.26 | 157.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.545 | 0.38913 | 161.26 | 157.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.642 | 0.9055 | 0.5 | 0.321 | 141.8 | 128.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.5 | 0.357 | 146.6 | 142.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.733 |  | 0.714 | 0.97408 | 0.415 | 0.29631 | 7.33 | 7.14
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.642 | 0.9055 | 0.415 | 0.26643 | 7.09 | 6.42
[11 empty] | Total | 2.758 | 942.58 | 897.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 942.58 | total F
|  | 0.72506 | SAIFI=total F/total customers
|  | 0.69018 | SAIDI=total G/total customers
|  | 0.9519 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 7.8788e-05 | ASUI=1-ASAI
|  | 2758.02 | ENS=total ENS*1000
|  | 2.1216 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 1.4355 | 0.93457 | 0.545 | 0.78235 | 337.92 | 315.81
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 2.3905 | 1.5563 | 0.545 | 1.3028 | 337.92 | 525.91
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 2.3905 | 1.5563 | 0.545 | 1.3028 | 337.92 | 525.91
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 3.3455 | 2.1781 | 0.545 | 1.8233 | 337.92 | 736.01
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 3.3455 | 2.1781 | 0.5 | 1.6727 | 307.2 | 669.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.536 |  | 4.013 | 2.6126 | 0.5 | 2.0065 | 307.2 | 802.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.415 | 2.0285 | 15.36 | 48.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.536 |  | 4.888 | 3.1823 | 0.415 | 2.0285 | 15.36 | 48.88
[11 empty] | Total | 12.9476 | 1996.8 | 3673.1
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 1996.8 | total F
|  | 1.536 | SAIFI=total F/total customers
|  | 2.8255 | SAIDI=total G/total customers
|  | 1.8395 | CAIDI=SAIDI/SAIFI
|  | 0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00032254 | ASUI=1-ASAI
|  | 12947.58 | ENS=total ENS*1000
|  | 9.9597 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1548
0.16 | 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 6192
0.16 |  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 4128
0.16 |  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 1892
0.16 |  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36 | [5 empty] | E | 1548
0.16 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4552
0.16 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.464 |  | 0.532 | 1.1466 | 1 | 0.532 | 0.464 | 0.532
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.556 | 1.178 | 1 | 0.556 | 0.472 | 0.556
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 0.46 | 1.0455 | 1 | 0.46 | 0.44 | 0.46
[10 empty] | Total | 1.548 | 1.376 | 1.548
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 0.516 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.8904e-05 | ASUI=1-ASAI
| 1548 | ENS=total ENS*1000
| 516 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 6.192 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 6192 | ENS=total ENS*1000
| 2064 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.464 |  | 1.392 | 3 | 1 | 1.392 | 0.464 | 1.392
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 1.32 | 3 | 1 | 1.32 | 0.44 | 1.32
[10 empty] | Total | 4.128 | 1.376 | 4.128
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 1.376 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015708 | ASUI=1-ASAI
| 4128 | ENS=total ENS*1000
| 1376 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.664 | 0.96512 | 1 | 0.664 | 0.688 | 0.664
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
[10 empty] | Total | 1.892 | 2.064 | 1.892
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.63067 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.1994e-05 | ASUI=1-ASAI
| 1892 | ENS=total ENS*1000
| 630.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.964 | 1.4012 | 1 | 0.964 | 0.688 | 0.964
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.524 | 2.2151 | 1 | 1.524 | 0.688 | 1.524
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 4.552 | 2.064 | 4.552
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.5173 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017321 | ASUI=1-ASAI
| 4552 | ENS=total ENS*1000
| 1517.3333 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1738
0.16 | 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 7224
0.16 |  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 5028
0.16 |  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 2104
0.16 |  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1738
0.16 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5484
0.16 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1 | 0.476 | 0.472 | 0.476
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 0.548 | 1.1048 | 1 | 0.548 | 0.496 | 0.548
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1.5 | 0.714 | 0.472 | 0.476
[10 empty] | Total | 1.738 | 1.44 | 1.5
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 0.5 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.7078e-05 | ASUI=1-ASAI
| 1738 | ENS=total ENS*1000
| 579.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 7.224 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 7224 | ENS=total ENS*1000
| 2408 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 1.488 | 3 | 1 | 1.488 | 0.496 | 1.488
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
[10 empty] | Total | 5.028 | 1.44 | 4.32
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 1.44 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016438 | ASUI=1-ASAI
| 5028 | ENS=total ENS*1000
| 1676 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1.5 | 0.876 | 0.688 | 0.584
[10 empty] | Total | 2.104 | 2.064 | 1.812
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.604 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.895e-05 | ASUI=1-ASAI
| 2104 | ENS=total ENS*1000
| 701.3333 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.884 | 1.2849 | 1 | 0.884 | 0.688 | 0.884
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.504 | 2.186 | 1 | 1.504 | 0.688 | 1.504
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 5.484 | 2.064 | 4.452
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.484 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016941 | ASUI=1-ASAI
| 5484 | ENS=total ENS*1000
| 1828 | AENS=ENS/total customers

## F7_(32-38)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.005 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2455.43
0.005 | 0.16 | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 16098.41
0.005 | 0.16 |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 8284.55
0.005 | 0.16 |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 4393.8725
0.005 | 0.16 |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 2455.43
0.005 | 0.16 |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | F | 10886.2225
0.005 | 0.16 |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.005 | 0.16 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.005 | 0.16 |  |  | x former |  |  | 0.005 | 10 | 0.05
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.005 | 0.16 |  |  | Calculation |  |  | 0.709 |  | 0.722 | 1.0183 | 0.545 | 0.39349 | 155.98 | 158.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.722 | 1.0183 | 0.545 | 0.39349 | 155.98 | 158.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.677 |  | 0.626 | 0.92467 | 0.545 | 0.34117 | 148.94 | 137.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 0.722 | 0.89689 | 0.545 | 0.39349 | 177.1 | 158.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 0.626 | 0.77764 | 0.5 | 0.313 | 161 | 125.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 0.722 | 0.89689 | 0.5 | 0.361 | 161 | 144.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 0.626 | 0.77764 | 0.415 | 0.25979 | 8.05 | 6.26
[11 empty] | Total | 2.4554 | 968.05 | 890.1
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 968.05 | total F
|  | 0.75043 | SAIFI=total F/total customers
|  | 0.69 | SAIDI=total G/total customers
|  | 0.91948 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 7.8767e-05 | ASUI=1-ASAI
|  | 2455.43 | ENS=total ENS*1000
|  | 1.9034 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.545 | 2.4405 | 310.42 | 985.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.545 | 2.4405 | 310.42 | 985.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.545 | 2.4405 | 310.42 | 985.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.545 | 2.4405 | 310.42 | 985.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.5 | 2.239 | 282.2 | 895.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.5 | 2.239 | 282.2 | 895.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.415 | 1.8584 | 14.11 | 44.78
[11 empty] | Total | 16.0984 | 1820.19 | 5776.62
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1820.19 | total F
|  | 1.411 | SAIFI=total F/total customers
|  | 4.478 | SAIDI=total G/total customers
|  | 3.1736 | CAIDI=SAIDI/SAIFI
|  | 0.99949 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00051119 | ASUI=1-ASAI
|  | 16098.41 | ENS=total ENS*1000
|  | 12.4794 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 2.162 | 3.0494 | 0.545 | 1.1783 | 155.98 | 475.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 2.162 | 3.0494 | 0.545 | 1.1783 | 155.98 | 475.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.677 |  | 2.066 | 3.0517 | 0.545 | 1.126 | 148.94 | 454.52
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 2.45 | 3.0435 | 0.545 | 1.3352 | 177.1 | 539
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 2.45 | 3.0435 | 0.5 | 1.225 | 161 | 490
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 2.45 | 3.0435 | 0.5 | 1.225 | 161 | 490
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 2.45 | 3.0435 | 0.415 | 1.0167 | 8.05 | 24.5
[11 empty] | Total | 8.2845 | 968.05 | 2949.3
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 968.05 | total F
|  | 0.75043 | SAIFI=total F/total customers
|  | 2.2863 | SAIDI=total G/total customers
|  | 3.0466 | CAIDI=SAIDI/SAIFI
|  | 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026099 | ASUI=1-ASAI
|  | 8284.55 | ENS=total ENS*1000
|  | 6.4221 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 1.073 | 0.76045 | 0.545 | 0.58478 | 310.42 | 236.06
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 1.073 | 0.76045 | 0.545 | 0.58478 | 310.42 | 236.06
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 1.3605 | 0.96421 | 0.545 | 0.74147 | 310.42 | 299.31
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 1.3605 | 0.96421 | 0.545 | 0.74147 | 310.42 | 299.31
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 0.993 | 0.70376 | 0.5 | 0.4965 | 282.2 | 198.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 1.3605 | 0.96421 | 0.5 | 0.68025 | 282.2 | 272.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 1.3605 | 0.96421 | 0.415 | 0.56461 | 14.11 | 13.605
[11 empty] | Total | 4.3939 | 1820.19 | 1555.045
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1820.19 | total F
|  | 1.411 | SAIFI=total F/total customers
|  | 1.2055 | SAIDI=total G/total customers
|  | 0.85433 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00013761 | ASUI=1-ASAI
|  | 4393.8725 | ENS=total ENS*1000
|  | 3.4061 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.722 | 1.0183 | 0.545 | 0.39349 | 155.98 | 158.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.709 |  | 0.722 | 1.0183 | 0.545 | 0.39349 | 155.98 | 158.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.677 |  | 0.626 | 0.92467 | 0.545 | 0.34117 | 148.94 | 137.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 0.722 | 0.89689 | 0.545 | 0.39349 | 177.1 | 158.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 0.626 | 0.77764 | 0.5 | 0.313 | 161 | 125.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 0.722 | 0.89689 | 0.5 | 0.361 | 161 | 144.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.805 |  | 0.626 | 0.77764 | 0.415 | 0.25979 | 8.05 | 6.26
[11 empty] | Total | 2.4554 | 968.05 | 890.1
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 968.05 | total F
|  | 0.75043 | SAIFI=total F/total customers
|  | 0.69 | SAIDI=total G/total customers
|  | 0.91948 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 7.8767e-05 | ASUI=1-ASAI
|  | 2455.43 | ENS=total ENS*1000
|  | 1.9034 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 1.373 | 0.97307 | 0.545 | 0.74829 | 310.42 | 302.06
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 1.9805 | 1.4036 | 0.545 | 1.0794 | 310.42 | 435.71
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 2.9355 | 2.0804 | 0.545 | 1.5998 | 310.42 | 645.81
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 2.9355 | 2.0804 | 0.545 | 1.5998 | 310.42 | 645.81
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | x former |  |  | 0.005 | 0.5 | 0.0025
|  |  |  | Calculation |  |  | 1.411 |  | 3.523 | 2.4968 | 0.5 | 1.7615 | 282.2 | 704.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.5 | 2.239 | 282.2 | 895.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | x former |  |  | 0.005 | 10 | 0.05
|  |  |  | Calculation |  |  | 1.411 |  | 4.478 | 3.1736 | 0.415 | 1.8584 | 14.11 | 44.78
[11 empty] | Total | 10.8862 | 1820.19 | 3674.37
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1820.19 | total F
|  | 1.411 | SAIFI=total F/total customers
|  | 2.8483 | SAIDI=total G/total customers
|  | 2.0187 | CAIDI=SAIDI/SAIFI
|  | 0.99967 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00032515 | ASUI=1-ASAI
|  | 10886.2225 | ENS=total ENS*1000
|  | 8.4389 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 2422.62 | 1100 | 15970.5 | 1100 | 7617.42 | 1100 | 4361.8125 | 1100 | 2422.62 | 1100 | 10725.6125 | 1100
Feeder 2 | 1828 | 3 | 7308 | 3 | 4908 | 3 | 2228 | 3 | 1828 | 3 | 5288 | 3
Feeder 3 | 2351.91 | 1080 | 15433.11 | 1080 | 7865.13 | 1080 | 4184.7475 | 1080 | 2351.91 | 1080 | 10388.735 | 1080
Feeder 4 | 2758.02 | 1300 | 19600.88 | 1300 | 8853.22 | 1300 | 5325.593 | 1300 | 2758.02 | 1300 | 12947.58 | 1300
Feeder 5 | 1548 | 3 | 6192 | 3 | 4128 | 3 | 1892 | 3 | 1548 | 3 | 4552 | 3
Feeder 6 | 1738 | 3 | 7224 | 3 | 5028 | 3 | 2104 | 3 | 1738 | 3 | 5484 | 3
Feeder 7 | 2455.43 | 1290 | 16098.41 | 1290 | 8284.55 | 1290 | 4393.873 | 1290 | 2455.43 | 1290 | 10886.22 | 1290
TOTAL | 15101.98 | 4779 | 87826.9 | 4779 | 46684.32 | 4779 | 24490.026 | 4779 | 15101.98 | 4779 | 60272.1475 | 4779
Analytic | 15.102 |  | 87.8269 |  | 46.6843 |  | 24.49 |  | 15.102 |  | 60.2721
Monte Carlo_Code | 15.096 |  | 87.793 |  | 45.477 |  | 24.486 |  | 15.101 |  | 60.26
Deviation | 0.039597 |  | 0.038599 |  | 2.5861 |  | 0.016439 |  | 0.0064892 |  | 0.020154
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 15.108 | 15.096 | 15.104 | 15.117 |  | 945000 | 87.833 | 87.793 | 87.84 | 87.781
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 45.477 | 45.453 | 45.397 | 45.43 |  | 47500 | 24.579 | 24.471 | 24.526 | 24.486
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 15.092 | 15.098 | 15.107 | 15.101 |  | 1140000 | 60.26 | 60.175 | 60.299 | 60.225