## F1_(1-7)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.01 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2598.12
0.01 | 0.16 | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 17199
0.01 | 0.16 |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 7792.92
0.01 | 0.16 |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 4679.025
0.01 | 0.16 |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 2598.12
0.01 | 0.16 |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 11466.525
0.01 | 0.16 |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
0.01 | 0.16 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | x former |  |  | 0.01 | 10 | 0.1
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | Calculation |  |  | 0.698 |  | 0.684 | 0.97994 | 0.545 | 0.37278 | 153.56 | 150.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.722 |  | 0.756 | 1.0471 | 0.545 | 0.41202 | 158.84 | 166.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 0.684 | 0.97994 | 0.545 | 0.37278 | 153.56 | 150.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 0.78 | 0.91765 | 0.545 | 0.4251 | 187 | 171.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 0.756 | 0.88941 | 0.5 | 0.378 | 170 | 151.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 0.78 | 0.91765 | 0.415 | 0.3237 | 8.5 | 7.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 0.756 | 0.88941 | 0.415 | 0.31374 | 8.5 | 7.56
[11 empty] | Total | 2.5981 | 839.96 | 805.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 839.96 | total F
|  | 0.7636 | SAIFI=total F/total customers
|  | 0.73222 | SAIDI=total G/total customers
|  | 0.9589 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.3587e-05 | ASUI=1-ASAI
|  | 2598.12 | ENS=total ENS*1000
|  | 2.3619 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.545 | 2.6705 | 323.4 | 1078
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.545 | 2.6705 | 323.4 | 1078
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.545 | 2.6705 | 323.4 | 1078
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.545 | 2.6705 | 323.4 | 1078
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.5 | 2.45 | 294 | 980
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.415 | 2.0335 | 14.7 | 49
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.415 | 2.0335 | 14.7 | 49
[11 empty] | Total | 17.199 | 1617 | 5390
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1617 | total F
|  | 1.47 | SAIFI=total F/total customers
|  | 4.9 | SAIDI=total G/total customers
|  | 3.3333 | CAIDI=SAIDI/SAIFI
|  | 0.99944 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00055936 | ASUI=1-ASAI
|  | 17199 | ENS=total ENS*1000
|  | 15.6355 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 2.164 | 3.1003 | 0.545 | 1.1794 | 153.56 | 476.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.722 |  | 2.236 | 3.097 | 0.545 | 1.2186 | 158.84 | 491.92
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 2.164 | 3.1003 | 0.545 | 1.1794 | 153.56 | 476.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 2.26 | 2.6588 | 0.545 | 1.2317 | 187 | 497.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 2.236 | 2.6306 | 0.5 | 1.118 | 170 | 447.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 2.26 | 2.6588 | 0.415 | 0.9379 | 8.5 | 22.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 2.236 | 2.6306 | 0.415 | 0.92794 | 8.5 | 22.36
[11 empty] | Total | 7.7929 | 839.96 | 2433.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 839.96 | total F
|  | 0.7636 | SAIFI=total F/total customers
|  | 2.2122 | SAIDI=total G/total customers
|  | 2.8971 | CAIDI=SAIDI/SAIFI
|  | 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00025254 | ASUI=1-ASAI
|  | 7792.92 | ENS=total ENS*1000
|  | 7.0845 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 1.07 | 0.72789 | 0.545 | 0.58315 | 323.4 | 235.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 1.13 | 0.76871 | 0.545 | 0.61585 | 323.4 | 248.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 1.07 | 0.72789 | 0.545 | 0.58315 | 323.4 | 235.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 1.545 | 1.051 | 0.545 | 0.84202 | 323.4 | 339.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 1.545 | 1.051 | 0.5 | 0.7725 | 294 | 309
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 1.545 | 1.051 | 0.415 | 0.64117 | 14.7 | 15.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 1.545 | 1.051 | 0.415 | 0.64117 | 14.7 | 15.45
[11 empty] | Total | 4.679 | 1617 | 1399.2
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1617 | total F
|  | 1.47 | SAIFI=total F/total customers
|  | 1.272 | SAIDI=total G/total customers
|  | 0.86531 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014521 | ASUI=1-ASAI
|  | 4679.025 | ENS=total ENS*1000
|  | 4.2537 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 0.684 | 0.97994 | 0.545 | 0.37278 | 153.56 | 150.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.722 |  | 0.756 | 1.0471 | 0.545 | 0.41202 | 158.84 | 166.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 0.684 | 0.97994 | 0.545 | 0.37278 | 153.56 | 150.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 0.78 | 0.91765 | 0.545 | 0.4251 | 187 | 171.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 0.756 | 0.88941 | 0.5 | 0.378 | 170 | 151.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 0.78 | 0.91765 | 0.415 | 0.3237 | 8.5 | 7.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.85 |  | 0.756 | 0.88941 | 0.415 | 0.31374 | 8.5 | 7.56
[11 empty] | Total | 2.5981 | 839.96 | 805.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 839.96 | total F
|  | 0.7636 | SAIFI=total F/total customers
|  | 0.73222 | SAIDI=total G/total customers
|  | 0.9589 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.3587e-05 | ASUI=1-ASAI
|  | 2598.12 | ENS=total ENS*1000
|  | 2.3619 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 1.37 | 0.93197 | 0.545 | 0.74665 | 323.4 | 301.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 2.085 | 1.4184 | 0.545 | 1.1363 | 323.4 | 458.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 2.74 | 1.8639 | 0.545 | 1.4933 | 323.4 | 602.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 3.85 | 2.619 | 0.545 | 2.0983 | 323.4 | 847
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.47 |  | 3.85 | 2.619 | 0.5 | 1.925 | 294 | 770
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.415 | 2.0335 | 14.7 | 49
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.47 |  | 4.9 | 3.3333 | 0.415 | 2.0335 | 14.7 | 49
[11 empty] | Total | 11.4665 | 1617 | 3077.9
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1617 | total F
|  | 1.47 | SAIFI=total F/total customers
|  | 2.7981 | SAIDI=total G/total customers
|  | 1.9035 | CAIDI=SAIDI/SAIFI
|  | 0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00031942 | ASUI=1-ASAI
|  | 11466.525 | ENS=total ENS*1000
|  | 10.4241 | AENS=ENS/total customers

## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1828
0.16 | 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 7308
0.16 |  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 4908
0.16 |  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | D | 2228
0.16 |  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1828
0.16 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5288
0.16 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.448 |  | 0.464 | 1.0357 | 1 | 0.464 | 0.448 | 0.464
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.536 | 1.1356 | 1.5 | 0.804 | 0.472 | 0.536
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 0.56 | 1.1667 | 1 | 0.56 | 0.48 | 0.56
[10 empty] | Total | 1.828 | 1.4 | 1.56
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 0.52 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.9361e-05 | ASUI=1-ASAI
| 1828 | ENS=total ENS*1000
| 609.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1.5 | 3.132 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 7.308 | 2.088 | 6.264
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 2.088 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023836 | ASUI=1-ASAI
| 7308 | ENS=total ENS*1000
| 2436 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.448 |  | 1.344 | 3 | 1 | 1.344 | 0.448 | 1.344
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 1.44 | 3 | 1 | 1.44 | 0.48 | 1.44
[10 empty] | Total | 4.908 | 1.4 | 4.2
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 1.4 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015982 | ASUI=1-ASAI
| 4908 | ENS=total ENS*1000
| 1636 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.588 | 0.84483 | 1 | 0.588 | 0.696 | 0.588
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.648 | 0.93103 | 1.5 | 0.972 | 0.696 | 0.648
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 0.668 | 0.95977 | 1 | 0.668 | 0.696 | 0.668
[10 empty] | Total | 2.228 | 2.088 | 1.904
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 0.63467 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.2451e-05 | ASUI=1-ASAI
| 2228 | ENS=total ENS*1000
| 742.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.908 | 1.3046 | 1 | 0.908 | 0.696 | 0.908
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 1.528 | 2.1954 | 1.5 | 2.292 | 0.696 | 1.528
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 5.288 | 2.088 | 4.524
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 1.508 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017215 | ASUI=1-ASAI
| 5288 | ENS=total ENS*1000
| 1762.6667 | AENS=ENS/total customers

## F3_(11-17)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.01 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2525.16
0.01 | 0.16 | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 16645.86
0.01 | 0.16 |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 8038.38
0.01 | 0.16 |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 4499.035
0.01 | 0.16 |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 2525.16
0.01 | 0.16 |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 11167.81
0.01 | 0.16 |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.01 | 0.16 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | x former |  |  | 0.01 | 10 | 0.1
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | Calculation |  |  | 0.706 |  | 0.768 | 1.0878 | 0.545 | 0.41856 | 155.32 | 168.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 0.744 | 1.0659 | 0.545 | 0.40548 | 153.56 | 163.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 0.744 | 1.0659 | 0.545 | 0.40548 | 153.56 | 163.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 0.672 | 0.84635 | 0.5 | 0.336 | 158.8 | 134.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 0.744 | 0.93703 | 0.5 | 0.372 | 158.8 | 148.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 0.744 | 0.93703 | 0.415 | 0.30876 | 7.94 | 7.44
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 0.672 | 0.84635 | 0.415 | 0.27888 | 7.94 | 6.72
[11 empty] | Total | 2.5252 | 795.92 | 793.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 795.92 | total F
|  | 0.73696 | SAIFI=total F/total customers
|  | 0.73489 | SAIDI=total G/total customers
|  | 0.99719 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.3891e-05 | ASUI=1-ASAI
|  | 2525.16 | ENS=total ENS*1000
|  | 2.3381 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.545 | 2.6182 | 316.36 | 1056.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.545 | 2.6182 | 316.36 | 1056.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.545 | 2.6182 | 316.36 | 1056.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.5 | 2.402 | 287.6 | 960.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.5 | 2.402 | 287.6 | 960.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.415 | 1.9937 | 14.38 | 48.04
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.415 | 1.9937 | 14.38 | 48.04
[11 empty] | Total | 16.6459 | 1553.04 | 5188.32
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1553.04 | total F
|  | 1.438 | SAIFI=total F/total customers
|  | 4.804 | SAIDI=total G/total customers
|  | 3.3408 | CAIDI=SAIDI/SAIFI
|  | 0.99945 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0005484 | ASUI=1-ASAI
|  | 16645.86 | ENS=total ENS*1000
|  | 15.4128 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.706 |  | 2.188 | 3.0992 | 0.545 | 1.1925 | 155.32 | 481.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 2.164 | 3.1003 | 0.545 | 1.1794 | 153.56 | 476.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 2.164 | 3.1003 | 0.545 | 1.1794 | 153.56 | 476.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 2.452 | 3.0882 | 0.5 | 1.226 | 158.8 | 490.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 2.452 | 3.0882 | 0.5 | 1.226 | 158.8 | 490.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 2.452 | 3.0882 | 0.415 | 1.0176 | 7.94 | 24.52
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 2.452 | 3.0882 | 0.415 | 1.0176 | 7.94 | 24.52
[11 empty] | Total | 8.0384 | 795.92 | 2463.36
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 795.92 | total F
|  | 0.73696 | SAIFI=total F/total customers
|  | 2.2809 | SAIDI=total G/total customers
|  | 3.095 | CAIDI=SAIDI/SAIFI
|  | 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026038 | ASUI=1-ASAI
|  | 8038.38 | ENS=total ENS*1000
|  | 7.4429 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 1.134 | 0.7886 | 0.545 | 0.61803 | 316.36 | 249.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 1.114 | 0.77469 | 0.545 | 0.60713 | 316.36 | 245.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 1.449 | 1.0076 | 0.545 | 0.7897 | 316.36 | 318.78
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 1.449 | 1.0076 | 0.5 | 0.7245 | 287.6 | 289.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 1.114 | 0.77469 | 0.5 | 0.557 | 287.6 | 222.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 1.449 | 1.0076 | 0.415 | 0.60133 | 14.38 | 14.49
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 1.449 | 1.0076 | 0.415 | 0.60133 | 14.38 | 14.49
[11 empty] | Total | 4.499 | 1553.04 | 1354.92
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1553.04 | total F
|  | 1.438 | SAIFI=total F/total customers
|  | 1.2546 | SAIDI=total G/total customers
|  | 0.87243 | CAIDI=SAIDI/SAIFI
|  | 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014321 | ASUI=1-ASAI
|  | 4499.035 | ENS=total ENS*1000
|  | 4.1658 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.706 |  | 0.768 | 1.0878 | 0.545 | 0.41856 | 155.32 | 168.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 0.744 | 1.0659 | 0.545 | 0.40548 | 153.56 | 163.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.698 |  | 0.744 | 1.0659 | 0.545 | 0.40548 | 153.56 | 163.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 0.672 | 0.84635 | 0.5 | 0.336 | 158.8 | 134.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 0.744 | 0.93703 | 0.5 | 0.372 | 158.8 | 148.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 0.744 | 0.93703 | 0.415 | 0.30876 | 7.94 | 7.44
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.794 |  | 0.672 | 0.84635 | 0.415 | 0.27888 | 7.94 | 6.72
[11 empty] | Total | 2.5252 | 795.92 | 793.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 795.92 | total F
|  | 0.73696 | SAIFI=total F/total customers
|  | 0.73489 | SAIDI=total G/total customers
|  | 0.99719 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.3891e-05 | ASUI=1-ASAI
|  | 2525.16 | ENS=total ENS*1000
|  | 2.3381 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 1.434 | 0.99722 | 0.545 | 0.78153 | 316.36 | 315.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 2.069 | 1.4388 | 0.545 | 1.1276 | 316.36 | 455.18
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 3.119 | 2.169 | 0.545 | 1.6999 | 316.36 | 686.18
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.438 |  | 3.119 | 2.169 | 0.5 | 1.5595 | 287.6 | 623.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.024 | 2.7983 | 0.5 | 2.012 | 287.6 | 804.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.415 | 1.9937 | 14.38 | 48.04
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.438 |  | 4.804 | 3.3408 | 0.415 | 1.9937 | 14.38 | 48.04
[11 empty] | Total | 11.1678 | 1553.04 | 2981.52
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1553.04 | total F
|  | 1.438 | SAIFI=total F/total customers
|  | 2.7607 | SAIDI=total G/total customers
|  | 1.9198 | CAIDI=SAIDI/SAIFI
|  | 0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00031514 | ASUI=1-ASAI
|  | 11167.81 | ENS=total ENS*1000
|  | 10.3406 | AENS=ENS/total customers

## F4_(18-25)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.01 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2958.52
0.01 | 0.16 | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 21204.88
0.01 | 0.16 |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 9053.72
0.01 | 0.16 |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 5737.105
0.01 | 0.16 |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 2958.52
0.01 | 0.16 |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 13915.08
0.01 | 0.16 |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
0.01 | 0.16 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | x former |  |  | 0.01 | 10 | 0.1
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.545 | 0.41638 | 162.36 | 168.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.692 | 0.96919 | 0.545 | 0.37714 | 157.08 | 152.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.545 | 0.41638 | 162.36 | 168.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.545 | 0.41638 | 162.36 | 168.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.692 | 0.96919 | 0.5 | 0.346 | 142.8 | 138.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.5 | 0.382 | 147.6 | 152.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.415 | 0.31706 | 7.38 | 7.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.692 | 0.96919 | 0.415 | 0.28718 | 7.14 | 6.92
[11 empty] | Total | 2.9585 | 949.08 | 962.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 949.08 | total F
|  | 0.73006 | SAIFI=total F/total customers
|  | 0.74018 | SAIDI=total G/total customers
|  | 1.0139 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.4496e-05 | ASUI=1-ASAI
|  | 2958.52 | ENS=total ENS*1000
|  | 2.2758 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.545 | 2.882 | 346.72 | 1163.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.545 | 2.882 | 346.72 | 1163.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.545 | 2.882 | 346.72 | 1163.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.545 | 2.882 | 346.72 | 1163.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.5 | 2.644 | 315.2 | 1057.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.5 | 2.644 | 315.2 | 1057.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.415 | 2.1945 | 15.76 | 52.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.415 | 2.1945 | 15.76 | 52.88
[11 empty] | Total | 21.2049 | 2048.8 | 6874.4
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2048.8 | total F
|  | 1.576 | SAIFI=total F/total customers
|  | 5.288 | SAIDI=total G/total customers
|  | 3.3553 | CAIDI=SAIDI/SAIFI
|  | 0.9994 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00060365 | ASUI=1-ASAI
|  | 21204.88 | ENS=total ENS*1000
|  | 16.3114 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 2.284 | 3.0949 | 0.545 | 1.2448 | 162.36 | 502.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 2.212 | 3.098 | 0.545 | 1.2055 | 157.08 | 486.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 2.284 | 3.0949 | 0.545 | 1.2448 | 162.36 | 502.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 2.284 | 3.0949 | 0.545 | 1.2448 | 162.36 | 502.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 2.212 | 3.098 | 0.5 | 1.106 | 142.8 | 442.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 2.284 | 3.0949 | 0.5 | 1.142 | 147.6 | 456.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 2.284 | 3.0949 | 0.415 | 0.94786 | 7.38 | 22.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 2.212 | 3.098 | 0.415 | 0.91798 | 7.14 | 22.12
[11 empty] | Total | 9.0537 | 949.08 | 2938.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 949.08 | total F
|  | 0.73006 | SAIFI=total F/total customers
|  | 2.2602 | SAIDI=total G/total customers
|  | 3.0959 | CAIDI=SAIDI/SAIFI
|  | 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00025801 | ASUI=1-ASAI
|  | 9053.72 | ENS=total ENS*1000
|  | 6.9644 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.183 | 0.75063 | 0.545 | 0.64473 | 346.72 | 260.26
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.518 | 0.9632 | 0.545 | 0.82731 | 346.72 | 333.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.518 | 0.9632 | 0.545 | 0.82731 | 346.72 | 333.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.518 | 0.9632 | 0.545 | 0.82731 | 346.72 | 333.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.518 | 0.9632 | 0.5 | 0.759 | 315.2 | 303.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.183 | 0.75063 | 0.5 | 0.5915 | 315.2 | 236.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.518 | 0.9632 | 0.415 | 0.62997 | 15.76 | 15.18
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.518 | 0.9632 | 0.415 | 0.62997 | 15.76 | 15.18
[11 empty] | Total | 5.7371 | 2048.8 | 1832.7
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2048.8 | total F
|  | 1.576 | SAIFI=total F/total customers
|  | 1.4098 | SAIDI=total G/total customers
|  | 0.89452 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00016093 | ASUI=1-ASAI
|  | 5737.105 | ENS=total ENS*1000
|  | 4.4132 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.545 | 0.41638 | 162.36 | 168.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.692 | 0.96919 | 0.545 | 0.37714 | 157.08 | 152.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.545 | 0.41638 | 162.36 | 168.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.545 | 0.41638 | 162.36 | 168.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.692 | 0.96919 | 0.5 | 0.346 | 142.8 | 138.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.5 | 0.382 | 147.6 | 152.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.738 |  | 0.764 | 1.0352 | 0.415 | 0.31706 | 7.38 | 7.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.692 | 0.96919 | 0.415 | 0.28718 | 7.14 | 6.92
[11 empty] | Total | 2.9585 | 949.08 | 962.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 949.08 | total F
|  | 0.73006 | SAIFI=total F/total customers
|  | 0.74018 | SAIDI=total G/total customers
|  | 1.0139 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.4496e-05 | ASUI=1-ASAI
|  | 2958.52 | ENS=total ENS*1000
|  | 2.2758 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 1.503 | 0.95368 | 0.545 | 0.81913 | 346.72 | 330.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 2.553 | 1.6199 | 0.545 | 1.3914 | 346.72 | 561.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 2.553 | 1.6199 | 0.545 | 1.3914 | 346.72 | 561.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 3.603 | 2.2862 | 0.545 | 1.9636 | 346.72 | 792.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 3.603 | 2.2862 | 0.5 | 1.8015 | 315.2 | 720.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.576 |  | 4.318 | 2.7398 | 0.5 | 2.159 | 315.2 | 863.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.415 | 2.1945 | 15.76 | 52.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.576 |  | 5.288 | 3.3553 | 0.415 | 2.1945 | 15.76 | 52.88
[11 empty] | Total | 13.9151 | 2048.8 | 3936.6
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2048.8 | total F
|  | 1.576 | SAIFI=total F/total customers
|  | 3.0282 | SAIDI=total G/total customers
|  | 1.9214 | CAIDI=SAIDI/SAIFI
|  | 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00034568 | ASUI=1-ASAI
|  | 13915.08 | ENS=total ENS*1000
|  | 10.7039 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1548
0.16 | 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 6192
0.16 |  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 4128
0.16 |  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 1892
0.16 |  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36 | [5 empty] | E | 1548
0.16 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4552
0.16 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.464 |  | 0.532 | 1.1466 | 1 | 0.532 | 0.464 | 0.532
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.556 | 1.178 | 1 | 0.556 | 0.472 | 0.556
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 0.46 | 1.0455 | 1 | 0.46 | 0.44 | 0.46
[10 empty] | Total | 1.548 | 1.376 | 1.548
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 0.516 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.8904e-05 | ASUI=1-ASAI
| 1548 | ENS=total ENS*1000
| 516 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 6.192 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 6192 | ENS=total ENS*1000
| 2064 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.464 |  | 1.392 | 3 | 1 | 1.392 | 0.464 | 1.392
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 1.32 | 3 | 1 | 1.32 | 0.44 | 1.32
[10 empty] | Total | 4.128 | 1.376 | 4.128
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 1.376 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015708 | ASUI=1-ASAI
| 4128 | ENS=total ENS*1000
| 1376 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.664 | 0.96512 | 1 | 0.664 | 0.688 | 0.664
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
[10 empty] | Total | 1.892 | 2.064 | 1.892
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.63067 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.1994e-05 | ASUI=1-ASAI
| 1892 | ENS=total ENS*1000
| 630.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.964 | 1.4012 | 1 | 0.964 | 0.688 | 0.964
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.524 | 2.2151 | 1 | 1.524 | 0.688 | 1.524
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 4.552 | 2.064 | 4.552
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.5173 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017321 | ASUI=1-ASAI
| 4552 | ENS=total ENS*1000
| 1517.3333 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1738
0.16 | 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 7224
0.16 |  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 5028
0.16 |  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 2104
0.16 |  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1738
0.16 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5484
0.16 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1 | 0.476 | 0.472 | 0.476
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 0.548 | 1.1048 | 1 | 0.548 | 0.496 | 0.548
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1.5 | 0.714 | 0.472 | 0.476
[10 empty] | Total | 1.738 | 1.44 | 1.5
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 0.5 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.7078e-05 | ASUI=1-ASAI
| 1738 | ENS=total ENS*1000
| 579.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 7.224 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 7224 | ENS=total ENS*1000
| 2408 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 1.488 | 3 | 1 | 1.488 | 0.496 | 1.488
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
[10 empty] | Total | 5.028 | 1.44 | 4.32
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 1.44 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016438 | ASUI=1-ASAI
| 5028 | ENS=total ENS*1000
| 1676 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1.5 | 0.876 | 0.688 | 0.584
[10 empty] | Total | 2.104 | 2.064 | 1.812
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.604 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.895e-05 | ASUI=1-ASAI
| 2104 | ENS=total ENS*1000
| 701.3333 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.884 | 1.2849 | 1 | 0.884 | 0.688 | 0.884
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.504 | 2.186 | 1 | 1.504 | 0.688 | 1.504
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 5.484 | 2.064 | 4.452
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.484 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016941 | ASUI=1-ASAI
| 5484 | ENS=total ENS*1000
| 1828 | AENS=ENS/total customers

## F7_(32-38)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.01 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2635.18
0.01 | 0.16 | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 17356.66
0.01 | 0.16 |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 8464.3
0.01 | 0.16 |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 4722.785
0.01 | 0.16 |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 2635.18
0.01 | 0.16 |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | F | 11656.885
0.01 | 0.16 |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.01 | 0.16 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.01 | 0.16 |  |  | x former |  |  | 0.01 | 10 | 0.1
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.01 | 0.16 |  |  | Calculation |  |  | 0.714 |  | 0.772 | 1.0812 | 0.545 | 0.42074 | 157.08 | 169.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.772 | 1.0812 | 0.545 | 0.42074 | 157.08 | 169.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.682 |  | 0.676 | 0.9912 | 0.545 | 0.36842 | 150.04 | 148.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 0.772 | 0.95309 | 0.545 | 0.42074 | 178.2 | 169.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 0.676 | 0.83457 | 0.5 | 0.338 | 162 | 135.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 0.772 | 0.95309 | 0.5 | 0.386 | 162 | 154.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 0.676 | 0.83457 | 0.415 | 0.28054 | 8.1 | 6.76
[11 empty] | Total | 2.6352 | 974.5 | 954.6
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 974.5 | total F
|  | 0.75543 | SAIFI=total F/total customers
|  | 0.74 | SAIDI=total G/total customers
|  | 0.97958 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.4475e-05 | ASUI=1-ASAI
|  | 2635.18 | ENS=total ENS*1000
|  | 2.0428 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.545 | 2.6313 | 318.12 | 1062.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.545 | 2.6313 | 318.12 | 1062.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.545 | 2.6313 | 318.12 | 1062.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.545 | 2.6313 | 318.12 | 1062.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.5 | 2.414 | 289.2 | 965.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.5 | 2.414 | 289.2 | 965.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.415 | 2.0036 | 14.46 | 48.28
[11 empty] | Total | 17.3567 | 1865.34 | 6228.12
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1865.34 | total F
|  | 1.446 | SAIFI=total F/total customers
|  | 4.828 | SAIDI=total G/total customers
|  | 3.3389 | CAIDI=SAIDI/SAIFI
|  | 0.99945 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00055114 | ASUI=1-ASAI
|  | 17356.66 | ENS=total ENS*1000
|  | 13.4548 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 2.212 | 3.098 | 0.545 | 1.2055 | 157.08 | 486.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 2.212 | 3.098 | 0.545 | 1.2055 | 157.08 | 486.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.682 |  | 2.116 | 3.1026 | 0.545 | 1.1532 | 150.04 | 465.52
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 2.5 | 3.0864 | 0.545 | 1.3625 | 178.2 | 550
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 2.5 | 3.0864 | 0.5 | 1.25 | 162 | 500
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 2.5 | 3.0864 | 0.5 | 1.25 | 162 | 500
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 2.5 | 3.0864 | 0.415 | 1.0375 | 8.1 | 25
[11 empty] | Total | 8.4643 | 974.5 | 3013.8
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 974.5 | total F
|  | 0.75543 | SAIFI=total F/total customers
|  | 2.3363 | SAIDI=total G/total customers
|  | 3.0927 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0002667 | ASUI=1-ASAI
|  | 8464.3 | ENS=total ENS*1000
|  | 6.5615 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 1.138 | 0.787 | 0.545 | 0.62021 | 318.12 | 250.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 1.138 | 0.787 | 0.545 | 0.62021 | 318.12 | 250.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 1.473 | 1.0187 | 0.545 | 0.80278 | 318.12 | 324.06
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 1.473 | 1.0187 | 0.545 | 0.80278 | 318.12 | 324.06
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 1.058 | 0.73167 | 0.5 | 0.529 | 289.2 | 211.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 1.473 | 1.0187 | 0.5 | 0.7365 | 289.2 | 294.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 1.473 | 1.0187 | 0.415 | 0.61129 | 14.46 | 14.73
[11 empty] | Total | 4.7228 | 1865.34 | 1669.77
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1865.34 | total F
|  | 1.446 | SAIFI=total F/total customers
|  | 1.2944 | SAIDI=total G/total customers
|  | 0.89516 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00014776 | ASUI=1-ASAI
|  | 4722.785 | ENS=total ENS*1000
|  | 3.6611 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.772 | 1.0812 | 0.545 | 0.42074 | 157.08 | 169.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.714 |  | 0.772 | 1.0812 | 0.545 | 0.42074 | 157.08 | 169.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.682 |  | 0.676 | 0.9912 | 0.545 | 0.36842 | 150.04 | 148.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 0.772 | 0.95309 | 0.545 | 0.42074 | 178.2 | 169.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 0.676 | 0.83457 | 0.5 | 0.338 | 162 | 135.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 0.772 | 0.95309 | 0.5 | 0.386 | 162 | 154.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.81 |  | 0.676 | 0.83457 | 0.415 | 0.28054 | 8.1 | 6.76
[11 empty] | Total | 2.6352 | 974.5 | 954.6
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 974.5 | total F
|  | 0.75543 | SAIFI=total F/total customers
|  | 0.74 | SAIDI=total G/total customers
|  | 0.97958 | CAIDI=SAIDI/SAIFI
|  | 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.4475e-05 | ASUI=1-ASAI
|  | 2635.18 | ENS=total ENS*1000
|  | 2.0428 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 1.438 | 0.99447 | 0.545 | 0.78371 | 318.12 | 316.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 2.093 | 1.4474 | 0.545 | 1.1407 | 318.12 | 460.46
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 3.143 | 2.1736 | 0.545 | 1.7129 | 318.12 | 691.46
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 3.143 | 2.1736 | 0.545 | 1.7129 | 318.12 | 691.46
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | x former |  |  | 0.01 | 0.5 | 0.005
|  |  |  | Calculation |  |  | 1.446 |  | 3.778 | 2.6127 | 0.5 | 1.889 | 289.2 | 755.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.5 | 2.414 | 289.2 | 965.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | x former |  |  | 0.01 | 10 | 0.1
|  |  |  | Calculation |  |  | 1.446 |  | 4.828 | 3.3389 | 0.415 | 2.0036 | 14.46 | 48.28
[11 empty] | Total | 11.6569 | 1865.34 | 3929.22
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1865.34 | total F
|  | 1.446 | SAIFI=total F/total customers
|  | 3.0459 | SAIDI=total G/total customers
|  | 2.1064 | CAIDI=SAIDI/SAIFI
|  | 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00034771 | ASUI=1-ASAI
|  | 11656.885 | ENS=total ENS*1000
|  | 9.0363 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 2598.12 | 1100 | 17199 | 1100 | 7792.92 | 1100 | 4679.025 | 1100 | 2598.12 | 1100 | 11466.525 | 1100
Feeder 2 | 1828 | 3 | 7308 | 3 | 4908 | 3 | 2228 | 3 | 1828 | 3 | 5288 | 3
Feeder 3 | 2525.16 | 1080 | 16645.86 | 1080 | 8038.38 | 1080 | 4499.035 | 1080 | 2525.16 | 1080 | 11167.81 | 1080
Feeder 4 | 2958.52 | 1300 | 21204.88 | 1300 | 9053.72 | 1300 | 5737.105 | 1300 | 2958.52 | 1300 | 13915.08 | 1300
Feeder 5 | 1548 | 3 | 6192 | 3 | 4128 | 3 | 1892 | 3 | 1548 | 3 | 4552 | 3
Feeder 6 | 1738 | 3 | 7224 | 3 | 5028 | 3 | 2104 | 3 | 1738 | 3 | 5484 | 3
Feeder 7 | 2635.18 | 1290 | 17356.66 | 1290 | 8464.3 | 1290 | 4722.785 | 1290 | 2635.18 | 1290 | 11656.89 | 1290
TOTAL | 15830.98 | 4779 | 93130.4 | 4779 | 47413.32 | 4779 | 25861.95 | 4779 | 15830.98 | 4779 | 63530.305 | 4779
Analytic | 15.831 |  | 93.1304 |  | 47.4133 |  | 25.862 |  | 15.831 |  | 63.5303
Monte Carlo_Code | 15.828 |  | 93.089 |  | 46.191 |  | 25.851 |  | 15.829 |  | 63.498
Deviation | 0.018824 |  | 0.044454 |  | 2.578 |  | 0.04234 |  | 0.012507 |  | 0.05085
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 15.827 | 15.828 | 15.836 | 15.832 |  | 945000 | 93.089 | 93.041 | 93.148 | 93.155
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 46.116 | 46.095 | 46.188 | 46.191 |  | 47500 | 25.879 | 25.872 | 25.851 | 25.872
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 15.827 | 15.829 | 15.837 | 15.836 |  | 1140000 | 63.498 | 63.463 | 63.401 | 63.453