## F1_(1-7)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.015 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2773.62
0.015 | 0.16 | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 18427.5
0.015 | 0.16 |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 7968.42
0.015 | 0.16 |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 4996.2375
0.015 | 0.16 |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 2773.62
0.015 | 0.16 |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 12207.4375
0.015 | 0.16 |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
0.015 | 0.16 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | x former |  |  | 0.015 | 10 | 0.15
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | Calculation |  |  | 0.703 |  | 0.734 | 1.0441 | 0.545 | 0.40003 | 154.66 | 161.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.727 |  | 0.806 | 1.1087 | 0.545 | 0.43927 | 159.94 | 177.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 0.734 | 1.0441 | 0.545 | 0.40003 | 154.66 | 161.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 0.83 | 0.97076 | 0.545 | 0.45235 | 188.1 | 182.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 0.806 | 0.94269 | 0.5 | 0.403 | 171 | 161.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 0.83 | 0.97076 | 0.415 | 0.34445 | 8.55 | 8.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 0.806 | 0.94269 | 0.415 | 0.33449 | 8.55 | 8.06
[11 empty] | Total | 2.7736 | 845.46 | 860.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 845.46 | total F
|  | 0.7686 | SAIFI=total F/total customers
|  | 0.78222 | SAIDI=total G/total customers
|  | 1.0177 | CAIDI=SAIDI/SAIFI
|  | 0.99991 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.9294e-05 | ASUI=1-ASAI
|  | 2773.62 | ENS=total ENS*1000
|  | 2.5215 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.545 | 2.8613 | 331.1 | 1155
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.545 | 2.8613 | 331.1 | 1155
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.545 | 2.8613 | 331.1 | 1155
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.545 | 2.8613 | 331.1 | 1155
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.5 | 2.625 | 301 | 1050
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.415 | 2.1788 | 15.05 | 52.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.415 | 2.1788 | 15.05 | 52.5
[11 empty] | Total | 18.4275 | 1655.5 | 5775
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1655.5 | total F
|  | 1.505 | SAIFI=total F/total customers
|  | 5.25 | SAIDI=total G/total customers
|  | 3.4884 | CAIDI=SAIDI/SAIFI
|  | 0.9994 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00059932 | ASUI=1-ASAI
|  | 18427.5 | ENS=total ENS*1000
|  | 16.7523 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 2.214 | 3.1494 | 0.545 | 1.2066 | 154.66 | 487.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.727 |  | 2.286 | 3.1444 | 0.545 | 1.2459 | 159.94 | 502.92
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 2.214 | 3.1494 | 0.545 | 1.2066 | 154.66 | 487.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 2.31 | 2.7018 | 0.545 | 1.259 | 188.1 | 508.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 2.286 | 2.6737 | 0.5 | 1.143 | 171 | 457.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 2.31 | 2.7018 | 0.415 | 0.95865 | 8.55 | 23.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 2.286 | 2.6737 | 0.415 | 0.94869 | 8.55 | 22.86
[11 empty] | Total | 7.9684 | 845.46 | 2488.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 845.46 | total F
|  | 0.7686 | SAIFI=total F/total customers
|  | 2.2622 | SAIDI=total G/total customers
|  | 2.9433 | CAIDI=SAIDI/SAIFI
|  | 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00025824 | ASUI=1-ASAI
|  | 7968.42 | ENS=total ENS*1000
|  | 7.244 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 1.135 | 0.75415 | 0.545 | 0.61858 | 331.1 | 249.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 1.195 | 0.79402 | 0.545 | 0.65128 | 331.1 | 262.9
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 1.135 | 0.75415 | 0.545 | 0.61858 | 331.1 | 249.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 1.6575 | 1.1013 | 0.545 | 0.90334 | 331.1 | 364.65
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 1.6575 | 1.1013 | 0.5 | 0.82875 | 301 | 331.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 1.6575 | 1.1013 | 0.415 | 0.68786 | 15.05 | 16.575
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 1.6575 | 1.1013 | 0.415 | 0.68786 | 15.05 | 16.575
[11 empty] | Total | 4.9962 | 1655.5 | 1491.6
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1655.5 | total F
|  | 1.505 | SAIFI=total F/total customers
|  | 1.356 | SAIDI=total G/total customers
|  | 0.901 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015479 | ASUI=1-ASAI
|  | 4996.2375 | ENS=total ENS*1000
|  | 4.542 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 0.734 | 1.0441 | 0.545 | 0.40003 | 154.66 | 161.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.727 |  | 0.806 | 1.1087 | 0.545 | 0.43927 | 159.94 | 177.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 0.734 | 1.0441 | 0.545 | 0.40003 | 154.66 | 161.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 0.83 | 0.97076 | 0.545 | 0.45235 | 188.1 | 182.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 0.806 | 0.94269 | 0.5 | 0.403 | 171 | 161.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 0.83 | 0.97076 | 0.415 | 0.34445 | 8.55 | 8.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.855 |  | 0.806 | 0.94269 | 0.415 | 0.33449 | 8.55 | 8.06
[11 empty] | Total | 2.7736 | 845.46 | 860.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 845.46 | total F
|  | 0.7686 | SAIFI=total F/total customers
|  | 0.78222 | SAIDI=total G/total customers
|  | 1.0177 | CAIDI=SAIDI/SAIFI
|  | 0.99991 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.9294e-05 | ASUI=1-ASAI
|  | 2773.62 | ENS=total ENS*1000
|  | 2.5215 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 1.435 | 0.95349 | 0.545 | 0.78208 | 331.1 | 315.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 2.1975 | 1.4601 | 0.545 | 1.1976 | 331.1 | 483.45
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 2.9 | 1.9269 | 0.545 | 1.5805 | 331.1 | 638
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 4.105 | 2.7276 | 0.545 | 2.2372 | 331.1 | 903.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.505 |  | 4.105 | 2.7276 | 0.5 | 2.0525 | 301 | 821
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.415 | 2.1788 | 15.05 | 52.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.505 |  | 5.25 | 3.4884 | 0.415 | 2.1788 | 15.05 | 52.5
[11 empty] | Total | 12.2074 | 1655.5 | 3266.25
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1655.5 | total F
|  | 1.505 | SAIFI=total F/total customers
|  | 2.9693 | SAIDI=total G/total customers
|  | 1.973 | CAIDI=SAIDI/SAIFI
|  | 0.99966 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00033896 | ASUI=1-ASAI
|  | 12207.4375 | ENS=total ENS*1000
|  | 11.0977 | AENS=ENS/total customers

## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1828
0.16 | 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 7308
0.16 |  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 4908
0.16 |  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | D | 2228
0.16 |  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1828
0.16 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5288
0.16 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.448 |  | 0.464 | 1.0357 | 1 | 0.464 | 0.448 | 0.464
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.536 | 1.1356 | 1.5 | 0.804 | 0.472 | 0.536
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 0.56 | 1.1667 | 1 | 0.56 | 0.48 | 0.56
[10 empty] | Total | 1.828 | 1.4 | 1.56
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 0.52 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.9361e-05 | ASUI=1-ASAI
| 1828 | ENS=total ENS*1000
| 609.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1.5 | 3.132 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 7.308 | 2.088 | 6.264
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 2.088 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023836 | ASUI=1-ASAI
| 7308 | ENS=total ENS*1000
| 2436 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.448 |  | 1.344 | 3 | 1 | 1.344 | 0.448 | 1.344
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 1.44 | 3 | 1 | 1.44 | 0.48 | 1.44
[10 empty] | Total | 4.908 | 1.4 | 4.2
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 1.4 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015982 | ASUI=1-ASAI
| 4908 | ENS=total ENS*1000
| 1636 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.588 | 0.84483 | 1 | 0.588 | 0.696 | 0.588
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.648 | 0.93103 | 1.5 | 0.972 | 0.696 | 0.648
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 0.668 | 0.95977 | 1 | 0.668 | 0.696 | 0.668
[10 empty] | Total | 2.228 | 2.088 | 1.904
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 0.63467 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.2451e-05 | ASUI=1-ASAI
| 2228 | ENS=total ENS*1000
| 742.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.908 | 1.3046 | 1 | 0.908 | 0.696 | 0.908
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 1.528 | 2.1954 | 1.5 | 2.292 | 0.696 | 1.528
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 5.288 | 2.088 | 4.524
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 1.508 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017215 | ASUI=1-ASAI
| 5288 | ENS=total ENS*1000
| 1762.6667 | AENS=ENS/total customers

## F3_(11-17)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.015 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2698.41
0.015 | 0.16 | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 17858.61
0.015 | 0.16 |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 8211.63
0.015 | 0.16 |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 4813.3225
0.015 | 0.16 |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 2698.41
0.015 | 0.16 |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 11946.885
0.015 | 0.16 |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.015 | 0.16 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | x former |  |  | 0.015 | 10 | 0.15
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | Calculation |  |  | 0.711 |  | 0.818 | 1.1505 | 0.545 | 0.44581 | 156.42 | 179.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 0.794 | 1.1294 | 0.545 | 0.43273 | 154.66 | 174.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 0.794 | 1.1294 | 0.545 | 0.43273 | 154.66 | 174.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 0.722 | 0.90363 | 0.5 | 0.361 | 159.8 | 144.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 0.794 | 0.99374 | 0.5 | 0.397 | 159.8 | 158.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 0.794 | 0.99374 | 0.415 | 0.32951 | 7.99 | 7.94
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 0.722 | 0.90363 | 0.415 | 0.29963 | 7.99 | 7.22
[11 empty] | Total | 2.6984 | 801.32 | 847.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 801.32 | total F
|  | 0.74196 | SAIFI=total F/total customers
|  | 0.78489 | SAIDI=total G/total customers
|  | 1.0579 | CAIDI=SAIDI/SAIFI
|  | 0.99991 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.9599e-05 | ASUI=1-ASAI
|  | 2698.41 | ENS=total ENS*1000
|  | 2.4985 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.545 | 2.8089 | 324.06 | 1133.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.545 | 2.8089 | 324.06 | 1133.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.545 | 2.8089 | 324.06 | 1133.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.5 | 2.577 | 294.6 | 1030.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.5 | 2.577 | 294.6 | 1030.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.415 | 2.1389 | 14.73 | 51.54
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.415 | 2.1389 | 14.73 | 51.54
[11 empty] | Total | 17.8586 | 1590.84 | 5566.32
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1590.84 | total F
|  | 1.473 | SAIFI=total F/total customers
|  | 5.154 | SAIDI=total G/total customers
|  | 3.499 | CAIDI=SAIDI/SAIFI
|  | 0.99941 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00058836 | ASUI=1-ASAI
|  | 17858.61 | ENS=total ENS*1000
|  | 16.5358 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.711 |  | 2.238 | 3.1477 | 0.545 | 1.2197 | 156.42 | 492.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 2.214 | 3.1494 | 0.545 | 1.2066 | 154.66 | 487.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 2.214 | 3.1494 | 0.545 | 1.2066 | 154.66 | 487.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 2.502 | 3.1314 | 0.5 | 1.251 | 159.8 | 500.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 2.502 | 3.1314 | 0.5 | 1.251 | 159.8 | 500.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 2.502 | 3.1314 | 0.415 | 1.0383 | 7.99 | 25.02
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 2.502 | 3.1314 | 0.415 | 1.0383 | 7.99 | 25.02
[11 empty] | Total | 8.2116 | 801.32 | 2517.36
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 801.32 | total F
|  | 0.74196 | SAIFI=total F/total customers
|  | 2.3309 | SAIDI=total G/total customers
|  | 3.1415 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026608 | ASUI=1-ASAI
|  | 8211.63 | ENS=total ENS*1000
|  | 7.6034 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 1.199 | 0.81399 | 0.545 | 0.65346 | 324.06 | 263.78
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 1.179 | 0.80041 | 0.545 | 0.64256 | 324.06 | 259.38
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 1.5615 | 1.0601 | 0.545 | 0.85102 | 324.06 | 343.53
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 1.5615 | 1.0601 | 0.5 | 0.78075 | 294.6 | 312.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 1.179 | 0.80041 | 0.5 | 0.5895 | 294.6 | 235.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 1.5615 | 1.0601 | 0.415 | 0.64802 | 14.73 | 15.615
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 1.5615 | 1.0601 | 0.415 | 0.64802 | 14.73 | 15.615
[11 empty] | Total | 4.8133 | 1590.84 | 1446.02
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1590.84 | total F
|  | 1.473 | SAIFI=total F/total customers
|  | 1.3389 | SAIDI=total G/total customers
|  | 0.90897 | CAIDI=SAIDI/SAIFI
|  | 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015284 | ASUI=1-ASAI
|  | 4813.3225 | ENS=total ENS*1000
|  | 4.4568 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.711 |  | 0.818 | 1.1505 | 0.545 | 0.44581 | 156.42 | 179.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 0.794 | 1.1294 | 0.545 | 0.43273 | 154.66 | 174.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.703 |  | 0.794 | 1.1294 | 0.545 | 0.43273 | 154.66 | 174.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 0.722 | 0.90363 | 0.5 | 0.361 | 159.8 | 144.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 0.794 | 0.99374 | 0.5 | 0.397 | 159.8 | 158.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 0.794 | 0.99374 | 0.415 | 0.32951 | 7.99 | 7.94
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.799 |  | 0.722 | 0.90363 | 0.415 | 0.29963 | 7.99 | 7.22
[11 empty] | Total | 2.6984 | 801.32 | 847.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 801.32 | total F
|  | 0.74196 | SAIFI=total F/total customers
|  | 0.78489 | SAIDI=total G/total customers
|  | 1.0579 | CAIDI=SAIDI/SAIFI
|  | 0.99991 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 8.9599e-05 | ASUI=1-ASAI
|  | 2698.41 | ENS=total ENS*1000
|  | 2.4985 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 1.499 | 1.0177 | 0.545 | 0.81696 | 324.06 | 329.78
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 2.1815 | 1.481 | 0.545 | 1.1889 | 324.06 | 479.93
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 3.3265 | 2.2583 | 0.545 | 1.8129 | 324.06 | 731.83
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.473 |  | 3.3265 | 2.2583 | 0.5 | 1.6632 | 294.6 | 665.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 4.374 | 2.9695 | 0.5 | 2.187 | 294.6 | 874.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.415 | 2.1389 | 14.73 | 51.54
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.473 |  | 5.154 | 3.499 | 0.415 | 2.1389 | 14.73 | 51.54
[11 empty] | Total | 11.9469 | 1590.84 | 3184.72
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1590.84 | total F
|  | 1.473 | SAIFI=total F/total customers
|  | 2.9488 | SAIDI=total G/total customers
|  | 2.0019 | CAIDI=SAIDI/SAIFI
|  | 0.99966 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00033662 | ASUI=1-ASAI
|  | 11946.885 | ENS=total ENS*1000
|  | 11.0619 | AENS=ENS/total customers

## F4_(18-25)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.015 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3159.02
0.015 | 0.16 | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 22808.88
0.015 | 0.16 |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 9254.22
0.015 | 0.16 |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 6148.6175
0.015 | 0.16 |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 3159.02
0.015 | 0.16 |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 14882.58
0.015 | 0.16 |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
0.015 | 0.16 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | x former |  |  | 0.015 | 10 | 0.15
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.545 | 0.44363 | 163.46 | 179.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.742 | 1.032 | 0.545 | 0.40439 | 158.18 | 163.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.545 | 0.44363 | 163.46 | 179.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.545 | 0.44363 | 163.46 | 179.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.742 | 1.032 | 0.5 | 0.371 | 143.8 | 148.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.5 | 0.407 | 148.6 | 162.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.415 | 0.33781 | 7.43 | 8.14
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.742 | 1.032 | 0.415 | 0.30793 | 7.19 | 7.42
[11 empty] | Total | 3.159 | 955.58 | 1027.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 955.58 | total F
|  | 0.73506 | SAIFI=total F/total customers
|  | 0.79018 | SAIDI=total G/total customers
|  | 1.075 | CAIDI=SAIDI/SAIFI
|  | 0.99991 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.0204e-05 | ASUI=1-ASAI
|  | 3159.02 | ENS=total ENS*1000
|  | 2.43 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.545 | 3.1 | 355.52 | 1251.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.545 | 3.1 | 355.52 | 1251.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.545 | 3.1 | 355.52 | 1251.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.545 | 3.1 | 355.52 | 1251.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.5 | 2.844 | 323.2 | 1137.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.5 | 2.844 | 323.2 | 1137.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.415 | 2.3605 | 16.16 | 56.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.415 | 2.3605 | 16.16 | 56.88
[11 empty] | Total | 22.8089 | 2100.8 | 7394.4
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2100.8 | total F
|  | 1.616 | SAIFI=total F/total customers
|  | 5.688 | SAIDI=total G/total customers
|  | 3.5198 | CAIDI=SAIDI/SAIFI
|  | 0.99935 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00064932 | ASUI=1-ASAI
|  | 22808.88 | ENS=total ENS*1000
|  | 17.5453 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 2.334 | 3.1413 | 0.545 | 1.272 | 163.46 | 513.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 2.262 | 3.146 | 0.545 | 1.2328 | 158.18 | 497.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 2.334 | 3.1413 | 0.545 | 1.272 | 163.46 | 513.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 2.334 | 3.1413 | 0.545 | 1.272 | 163.46 | 513.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 2.262 | 3.146 | 0.5 | 1.131 | 143.8 | 452.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 2.334 | 3.1413 | 0.5 | 1.167 | 148.6 | 466.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 2.334 | 3.1413 | 0.415 | 0.96861 | 7.43 | 23.34
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 2.262 | 3.146 | 0.415 | 0.93873 | 7.19 | 22.62
[11 empty] | Total | 9.2542 | 955.58 | 3003.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 955.58 | total F
|  | 0.73506 | SAIFI=total F/total customers
|  | 2.3102 | SAIDI=total G/total customers
|  | 3.1428 | CAIDI=SAIDI/SAIFI
|  | 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026372 | ASUI=1-ASAI
|  | 9254.22 | ENS=total ENS*1000
|  | 7.1186 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.2505 | 0.77382 | 0.545 | 0.68152 | 355.52 | 275.11
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.633 | 1.0105 | 0.545 | 0.88999 | 355.52 | 359.26
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.633 | 1.0105 | 0.545 | 0.88999 | 355.52 | 359.26
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.633 | 1.0105 | 0.545 | 0.88999 | 355.52 | 359.26
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.633 | 1.0105 | 0.5 | 0.8165 | 323.2 | 326.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.2505 | 0.77382 | 0.5 | 0.62525 | 323.2 | 250.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.633 | 1.0105 | 0.415 | 0.6777 | 16.16 | 16.33
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.633 | 1.0105 | 0.415 | 0.6777 | 16.16 | 16.33
[11 empty] | Total | 6.1486 | 2100.8 | 1962.25
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2100.8 | total F
|  | 1.616 | SAIFI=total F/total customers
|  | 1.5094 | SAIDI=total G/total customers
|  | 0.93405 | CAIDI=SAIDI/SAIFI
|  | 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00017231 | ASUI=1-ASAI
|  | 6148.6175 | ENS=total ENS*1000
|  | 4.7297 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.545 | 0.44363 | 163.46 | 179.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.742 | 1.032 | 0.545 | 0.40439 | 158.18 | 163.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.545 | 0.44363 | 163.46 | 179.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.545 | 0.44363 | 163.46 | 179.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.742 | 1.032 | 0.5 | 0.371 | 143.8 | 148.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.5 | 0.407 | 148.6 | 162.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.743 |  | 0.814 | 1.0956 | 0.415 | 0.33781 | 7.43 | 8.14
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.742 | 1.032 | 0.415 | 0.30793 | 7.19 | 7.42
[11 empty] | Total | 3.159 | 955.58 | 1027.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 955.58 | total F
|  | 0.73506 | SAIFI=total F/total customers
|  | 0.79018 | SAIDI=total G/total customers
|  | 1.075 | CAIDI=SAIDI/SAIFI
|  | 0.99991 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.0204e-05 | ASUI=1-ASAI
|  | 3159.02 | ENS=total ENS*1000
|  | 2.43 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 1.5705 | 0.97184 | 0.545 | 0.85592 | 355.52 | 345.51
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 2.7155 | 1.6804 | 0.545 | 1.4799 | 355.52 | 597.41
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 2.7155 | 1.6804 | 0.545 | 1.4799 | 355.52 | 597.41
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 3.8605 | 2.3889 | 0.545 | 2.104 | 355.52 | 849.31
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 3.8605 | 2.3889 | 0.5 | 1.9302 | 323.2 | 772.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.616 |  | 4.623 | 2.8608 | 0.5 | 2.3115 | 323.2 | 924.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.415 | 2.3605 | 16.16 | 56.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.616 |  | 5.688 | 3.5198 | 0.415 | 2.3605 | 16.16 | 56.88
[11 empty] | Total | 14.8826 | 2100.8 | 4200.1
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2100.8 | total F
|  | 1.616 | SAIFI=total F/total customers
|  | 3.2308 | SAIDI=total G/total customers
|  | 1.9993 | CAIDI=SAIDI/SAIFI
|  | 0.99963 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00036882 | ASUI=1-ASAI
|  | 14882.58 | ENS=total ENS*1000
|  | 11.4481 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1548
0.16 | 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 6192
0.16 |  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 4128
0.16 |  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 1892
0.16 |  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36 | [5 empty] | E | 1548
0.16 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4552
0.16 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.464 |  | 0.532 | 1.1466 | 1 | 0.532 | 0.464 | 0.532
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.556 | 1.178 | 1 | 0.556 | 0.472 | 0.556
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 0.46 | 1.0455 | 1 | 0.46 | 0.44 | 0.46
[10 empty] | Total | 1.548 | 1.376 | 1.548
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 0.516 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.8904e-05 | ASUI=1-ASAI
| 1548 | ENS=total ENS*1000
| 516 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 6.192 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 6192 | ENS=total ENS*1000
| 2064 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.464 |  | 1.392 | 3 | 1 | 1.392 | 0.464 | 1.392
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 1.32 | 3 | 1 | 1.32 | 0.44 | 1.32
[10 empty] | Total | 4.128 | 1.376 | 4.128
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 1.376 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015708 | ASUI=1-ASAI
| 4128 | ENS=total ENS*1000
| 1376 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.664 | 0.96512 | 1 | 0.664 | 0.688 | 0.664
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
[10 empty] | Total | 1.892 | 2.064 | 1.892
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.63067 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.1994e-05 | ASUI=1-ASAI
| 1892 | ENS=total ENS*1000
| 630.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.964 | 1.4012 | 1 | 0.964 | 0.688 | 0.964
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.524 | 2.2151 | 1 | 1.524 | 0.688 | 1.524
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 4.552 | 2.064 | 4.552
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.5173 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017321 | ASUI=1-ASAI
| 4552 | ENS=total ENS*1000
| 1517.3333 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1738
0.16 | 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 7224
0.16 |  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 5028
0.16 |  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 2104
0.16 |  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1738
0.16 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5484
0.16 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1 | 0.476 | 0.472 | 0.476
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 0.548 | 1.1048 | 1 | 0.548 | 0.496 | 0.548
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1.5 | 0.714 | 0.472 | 0.476
[10 empty] | Total | 1.738 | 1.44 | 1.5
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 0.5 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.7078e-05 | ASUI=1-ASAI
| 1738 | ENS=total ENS*1000
| 579.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 7.224 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 7224 | ENS=total ENS*1000
| 2408 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 1.488 | 3 | 1 | 1.488 | 0.496 | 1.488
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
[10 empty] | Total | 5.028 | 1.44 | 4.32
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 1.44 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016438 | ASUI=1-ASAI
| 5028 | ENS=total ENS*1000
| 1676 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1.5 | 0.876 | 0.688 | 0.584
[10 empty] | Total | 2.104 | 2.064 | 1.812
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.604 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.895e-05 | ASUI=1-ASAI
| 2104 | ENS=total ENS*1000
| 701.3333 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.884 | 1.2849 | 1 | 0.884 | 0.688 | 0.884
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.504 | 2.186 | 1 | 1.504 | 0.688 | 1.504
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 5.484 | 2.064 | 4.452
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.484 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016941 | ASUI=1-ASAI
| 5484 | ENS=total ENS*1000
| 1828 | AENS=ENS/total customers

## F7_(32-38)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.015 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2814.93
0.015 | 0.16 | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 18614.91
0.015 | 0.16 |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 8644.05
0.015 | 0.16 |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 5051.6975
0.015 | 0.16 |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 2814.93
0.015 | 0.16 |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | F | 12427.5475
0.015 | 0.16 |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.015 | 0.16 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.015 | 0.16 |  |  | x former |  |  | 0.015 | 10 | 0.15
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.015 | 0.16 |  |  | Calculation |  |  | 0.719 |  | 0.822 | 1.1433 | 0.545 | 0.44799 | 158.18 | 180.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.822 | 1.1433 | 0.545 | 0.44799 | 158.18 | 180.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.687 |  | 0.726 | 1.0568 | 0.545 | 0.39567 | 151.14 | 159.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 0.822 | 1.0086 | 0.545 | 0.44799 | 179.3 | 180.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 0.726 | 0.8908 | 0.5 | 0.363 | 163 | 145.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 0.822 | 1.0086 | 0.5 | 0.411 | 163 | 164.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 0.726 | 0.8908 | 0.415 | 0.30129 | 8.15 | 7.26
[11 empty] | Total | 2.8149 | 980.95 | 1019.1
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 980.95 | total F
|  | 0.76043 | SAIFI=total F/total customers
|  | 0.79 | SAIDI=total G/total customers
|  | 1.0389 | CAIDI=SAIDI/SAIFI
|  | 0.99991 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.0183e-05 | ASUI=1-ASAI
|  | 2814.93 | ENS=total ENS*1000
|  | 2.1821 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.545 | 2.822 | 325.82 | 1139.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.545 | 2.822 | 325.82 | 1139.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.545 | 2.822 | 325.82 | 1139.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.545 | 2.822 | 325.82 | 1139.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.5 | 2.589 | 296.2 | 1035.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.5 | 2.589 | 296.2 | 1035.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.415 | 2.1489 | 14.81 | 51.78
[11 empty] | Total | 18.6149 | 1910.49 | 6679.62
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1910.49 | total F
|  | 1.481 | SAIFI=total F/total customers
|  | 5.178 | SAIDI=total G/total customers
|  | 3.4963 | CAIDI=SAIDI/SAIFI
|  | 0.99941 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0005911 | ASUI=1-ASAI
|  | 18614.91 | ENS=total ENS*1000
|  | 14.4302 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 2.262 | 3.146 | 0.545 | 1.2328 | 158.18 | 497.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 2.262 | 3.146 | 0.545 | 1.2328 | 158.18 | 497.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.687 |  | 2.166 | 3.1528 | 0.545 | 1.1805 | 151.14 | 476.52
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 2.55 | 3.1288 | 0.545 | 1.3897 | 179.3 | 561
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 2.55 | 3.1288 | 0.5 | 1.275 | 163 | 510
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 2.55 | 3.1288 | 0.5 | 1.275 | 163 | 510
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 2.55 | 3.1288 | 0.415 | 1.0582 | 8.15 | 25.5
[11 empty] | Total | 8.644 | 980.95 | 3078.3
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 980.95 | total F
|  | 0.76043 | SAIFI=total F/total customers
|  | 2.3863 | SAIDI=total G/total customers
|  | 3.1381 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00027241 | ASUI=1-ASAI
|  | 8644.05 | ENS=total ENS*1000
|  | 6.7008 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 1.203 | 0.81229 | 0.545 | 0.65564 | 325.82 | 264.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 1.203 | 0.81229 | 0.545 | 0.65564 | 325.82 | 264.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 1.5855 | 1.0706 | 0.545 | 0.8641 | 325.82 | 348.81
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 1.5855 | 1.0706 | 0.545 | 0.8641 | 325.82 | 348.81
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 1.123 | 0.75827 | 0.5 | 0.5615 | 296.2 | 224.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 1.5855 | 1.0706 | 0.5 | 0.79275 | 296.2 | 317.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 1.5855 | 1.0706 | 0.415 | 0.65798 | 14.81 | 15.855
[11 empty] | Total | 5.0517 | 1910.49 | 1784.495
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1910.49 | total F
|  | 1.481 | SAIFI=total F/total customers
|  | 1.3833 | SAIDI=total G/total customers
|  | 0.93405 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00015791 | ASUI=1-ASAI
|  | 5051.6975 | ENS=total ENS*1000
|  | 3.916 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.822 | 1.1433 | 0.545 | 0.44799 | 158.18 | 180.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.719 |  | 0.822 | 1.1433 | 0.545 | 0.44799 | 158.18 | 180.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.687 |  | 0.726 | 1.0568 | 0.545 | 0.39567 | 151.14 | 159.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 0.822 | 1.0086 | 0.545 | 0.44799 | 179.3 | 180.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 0.726 | 0.8908 | 0.5 | 0.363 | 163 | 145.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 0.822 | 1.0086 | 0.5 | 0.411 | 163 | 164.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.815 |  | 0.726 | 0.8908 | 0.415 | 0.30129 | 8.15 | 7.26
[11 empty] | Total | 2.8149 | 980.95 | 1019.1
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 980.95 | total F
|  | 0.76043 | SAIFI=total F/total customers
|  | 0.79 | SAIDI=total G/total customers
|  | 1.0389 | CAIDI=SAIDI/SAIFI
|  | 0.99991 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.0183e-05 | ASUI=1-ASAI
|  | 2814.93 | ENS=total ENS*1000
|  | 2.1821 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 1.503 | 1.0149 | 0.545 | 0.81914 | 325.82 | 330.66
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 2.2055 | 1.4892 | 0.545 | 1.202 | 325.82 | 485.21
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 3.3505 | 2.2623 | 0.545 | 1.826 | 325.82 | 737.11
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 3.3505 | 2.2623 | 0.545 | 1.826 | 325.82 | 737.11
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | x former |  |  | 0.015 | 0.5 | 0.0075
|  |  |  | Calculation |  |  | 1.481 |  | 4.033 | 2.7232 | 0.5 | 2.0165 | 296.2 | 806.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.5 | 2.589 | 296.2 | 1035.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  |  | Calculation |  |  | 1.481 |  | 5.178 | 3.4963 | 0.415 | 2.1489 | 14.81 | 51.78
[11 empty] | Total | 12.4275 | 1910.49 | 4184.07
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1910.49 | total F
|  | 1.481 | SAIFI=total F/total customers
|  | 3.2435 | SAIDI=total G/total customers
|  | 2.1901 | CAIDI=SAIDI/SAIFI
|  | 0.99963 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00037026 | ASUI=1-ASAI
|  | 12427.5475 | ENS=total ENS*1000
|  | 9.6338 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 2773.62 | 1100 | 18427.5 | 1100 | 7968.42 | 1100 | 4996.2375 | 1100 | 2773.62 | 1100 | 12207.4375 | 1100
Feeder 2 | 1828 | 3 | 7308 | 3 | 4908 | 3 | 2228 | 3 | 1828 | 3 | 5288 | 3
Feeder 3 | 2698.41 | 1080 | 17858.61 | 1080 | 8211.63 | 1080 | 4813.3225 | 1080 | 2698.41 | 1080 | 11946.885 | 1080
Feeder 4 | 3159.02 | 1300 | 22808.88 | 1300 | 9254.22 | 1300 | 6148.618 | 1300 | 3159.02 | 1300 | 14882.58 | 1300
Feeder 5 | 1548 | 3 | 6192 | 3 | 4128 | 3 | 1892 | 3 | 1548 | 3 | 4552 | 3
Feeder 6 | 1738 | 3 | 7224 | 3 | 5028 | 3 | 2104 | 3 | 1738 | 3 | 5484 | 3
Feeder 7 | 2814.93 | 1290 | 18614.91 | 1290 | 8644.05 | 1290 | 5051.698 | 1290 | 2814.93 | 1290 | 12427.55 | 1290
TOTAL | 16559.98 | 4779 | 98433.9 | 4779 | 48142.32 | 4779 | 27233.876 | 4779 | 16559.98 | 4779 | 66788.4525 | 4779
Analytic | 16.56 |  | 98.4339 |  | 48.1423 |  | 27.2339 |  | 16.56 |  | 66.7885
Monte Carlo_Code | 16.559 |  | 98.401 |  | 46.931 |  | 27.233 |  | 16.558 |  | 66.677
Deviation | 0.0059179 |  | 0.033423 |  | 2.5161 |  | 0.0032166 |  | 0.011957 |  | 0.16687
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 16.563 | 16.569 | 16.549 | 16.559 |  | 945000 | 98.449 | 98.401 | 98.487 | 98.446
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 46.86 | 46.919 | 46.918 | 46.931 |  | 47500 | 27.232 | 27.239 | 27.233 | 27.235
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 16.576 | 16.574 | 16.568 | 16.558 |  | 1140000 | 66.638 | 66.677 | 66.673 | 66.642