## F1_(1-7)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.02 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2949.12
0.02 | 0.16 | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 19656
0.02 | 0.16 |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 8143.92
0.02 | 0.16 |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 5313.45
0.02 | 0.16 |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 2949.12
0.02 | 0.16 |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 12948.35
0.02 | 0.16 |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
0.02 | 0.16 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | x former |  |  | 0.02 | 10 | 0.2
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | Calculation |  |  | 0.708 |  | 0.784 | 1.1073 | 0.545 | 0.42728 | 155.76 | 172.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.732 |  | 0.856 | 1.1694 | 0.545 | 0.46652 | 161.04 | 188.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 0.784 | 1.1073 | 0.545 | 0.42728 | 155.76 | 172.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 0.88 | 1.0233 | 0.545 | 0.4796 | 189.2 | 193.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 0.856 | 0.99535 | 0.5 | 0.428 | 172 | 171.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 0.88 | 1.0233 | 0.415 | 0.3652 | 8.6 | 8.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 0.856 | 0.99535 | 0.415 | 0.35524 | 8.6 | 8.56
[11 empty] | Total | 2.9491 | 850.96 | 915.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 850.96 | total F
|  | 0.7736 | SAIFI=total F/total customers
|  | 0.83222 | SAIDI=total G/total customers
|  | 1.0758 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.5002e-05 | ASUI=1-ASAI
|  | 2949.12 | ENS=total ENS*1000
|  | 2.681 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.545 | 3.052 | 338.8 | 1232
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.545 | 3.052 | 338.8 | 1232
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.545 | 3.052 | 338.8 | 1232
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.545 | 3.052 | 338.8 | 1232
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.5 | 2.8 | 308 | 1120
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.415 | 2.324 | 15.4 | 56
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.415 | 2.324 | 15.4 | 56
[11 empty] | Total | 19.656 | 1694 | 6160
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1694 | total F
|  | 1.54 | SAIFI=total F/total customers
|  | 5.6 | SAIDI=total G/total customers
|  | 3.6364 | CAIDI=SAIDI/SAIFI
|  | 0.99936 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00063927 | ASUI=1-ASAI
|  | 19656 | ENS=total ENS*1000
|  | 17.8691 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 2.264 | 3.1977 | 0.545 | 1.2339 | 155.76 | 498.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.732 |  | 2.336 | 3.1913 | 0.545 | 1.2731 | 161.04 | 513.92
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 2.264 | 3.1977 | 0.545 | 1.2339 | 155.76 | 498.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 2.36 | 2.7442 | 0.545 | 1.2862 | 189.2 | 519.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 2.336 | 2.7163 | 0.5 | 1.168 | 172 | 467.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 2.36 | 2.7442 | 0.415 | 0.9794 | 8.6 | 23.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 2.336 | 2.7163 | 0.415 | 0.96944 | 8.6 | 23.36
[11 empty] | Total | 8.1439 | 850.96 | 2543.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 850.96 | total F
|  | 0.7736 | SAIFI=total F/total customers
|  | 2.3122 | SAIDI=total G/total customers
|  | 2.9889 | CAIDI=SAIDI/SAIFI
|  | 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026395 | ASUI=1-ASAI
|  | 8143.92 | ENS=total ENS*1000
|  | 7.4036 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 1.2 | 0.77922 | 0.545 | 0.654 | 338.8 | 264
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 1.26 | 0.81818 | 0.545 | 0.6867 | 338.8 | 277.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 1.2 | 0.77922 | 0.545 | 0.654 | 338.8 | 264
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 1.77 | 1.1494 | 0.545 | 0.96465 | 338.8 | 389.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 1.77 | 1.1494 | 0.5 | 0.885 | 308 | 354
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 1.77 | 1.1494 | 0.415 | 0.73455 | 15.4 | 17.7
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 1.77 | 1.1494 | 0.415 | 0.73455 | 15.4 | 17.7
[11 empty] | Total | 5.3134 | 1694 | 1584
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1694 | total F
|  | 1.54 | SAIFI=total F/total customers
|  | 1.44 | SAIDI=total G/total customers
|  | 0.93506 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00016438 | ASUI=1-ASAI
|  | 5313.45 | ENS=total ENS*1000
|  | 4.8304 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 0.784 | 1.1073 | 0.545 | 0.42728 | 155.76 | 172.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.732 |  | 0.856 | 1.1694 | 0.545 | 0.46652 | 161.04 | 188.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 0.784 | 1.1073 | 0.545 | 0.42728 | 155.76 | 172.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 0.88 | 1.0233 | 0.545 | 0.4796 | 189.2 | 193.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 0.856 | 0.99535 | 0.5 | 0.428 | 172 | 171.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 0.88 | 1.0233 | 0.415 | 0.3652 | 8.6 | 8.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.86 |  | 0.856 | 0.99535 | 0.415 | 0.35524 | 8.6 | 8.56
[11 empty] | Total | 2.9491 | 850.96 | 915.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 850.96 | total F
|  | 0.7736 | SAIFI=total F/total customers
|  | 0.83222 | SAIDI=total G/total customers
|  | 1.0758 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.5002e-05 | ASUI=1-ASAI
|  | 2949.12 | ENS=total ENS*1000
|  | 2.681 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 1.5 | 0.97403 | 0.545 | 0.8175 | 338.8 | 330
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 2.31 | 1.5 | 0.545 | 1.2589 | 338.8 | 508.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 3.06 | 1.987 | 0.545 | 1.6677 | 338.8 | 673.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 4.36 | 2.8312 | 0.545 | 2.3762 | 338.8 | 959.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.54 |  | 4.36 | 2.8312 | 0.5 | 2.18 | 308 | 872
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.415 | 2.324 | 15.4 | 56
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.54 |  | 5.6 | 3.6364 | 0.415 | 2.324 | 15.4 | 56
[11 empty] | Total | 12.9484 | 1694 | 3454.6
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1694 | total F
|  | 1.54 | SAIFI=total F/total customers
|  | 3.1405 | SAIDI=total G/total customers
|  | 2.0393 | CAIDI=SAIDI/SAIFI
|  | 0.99964 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00035851 | ASUI=1-ASAI
|  | 12948.35 | ENS=total ENS*1000
|  | 11.7712 | AENS=ENS/total customers

## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1828
0.16 | 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 7308
0.16 |  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 4908
0.16 |  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | D | 2228
0.16 |  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1828
0.16 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5288
0.16 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.448 |  | 0.464 | 1.0357 | 1 | 0.464 | 0.448 | 0.464
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.536 | 1.1356 | 1.5 | 0.804 | 0.472 | 0.536
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 0.56 | 1.1667 | 1 | 0.56 | 0.48 | 0.56
[10 empty] | Total | 1.828 | 1.4 | 1.56
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 0.52 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.9361e-05 | ASUI=1-ASAI
| 1828 | ENS=total ENS*1000
| 609.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1.5 | 3.132 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 7.308 | 2.088 | 6.264
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 2.088 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023836 | ASUI=1-ASAI
| 7308 | ENS=total ENS*1000
| 2436 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.448 |  | 1.344 | 3 | 1 | 1.344 | 0.448 | 1.344
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 1.44 | 3 | 1 | 1.44 | 0.48 | 1.44
[10 empty] | Total | 4.908 | 1.4 | 4.2
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 1.4 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015982 | ASUI=1-ASAI
| 4908 | ENS=total ENS*1000
| 1636 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.588 | 0.84483 | 1 | 0.588 | 0.696 | 0.588
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.648 | 0.93103 | 1.5 | 0.972 | 0.696 | 0.648
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 0.668 | 0.95977 | 1 | 0.668 | 0.696 | 0.668
[10 empty] | Total | 2.228 | 2.088 | 1.904
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 0.63467 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.2451e-05 | ASUI=1-ASAI
| 2228 | ENS=total ENS*1000
| 742.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.908 | 1.3046 | 1 | 0.908 | 0.696 | 0.908
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 1.528 | 2.1954 | 1.5 | 2.292 | 0.696 | 1.528
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 5.288 | 2.088 | 4.524
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 1.508 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017215 | ASUI=1-ASAI
| 5288 | ENS=total ENS*1000
| 1762.6667 | AENS=ENS/total customers

## F3_(11-17)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.02 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2871.66
0.02 | 0.16 | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 19071.36
0.02 | 0.16 |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 8384.88
0.02 | 0.16 |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 5127.61
0.02 | 0.16 |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 2871.66
0.02 | 0.16 |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 12725.96
0.02 | 0.16 |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.02 | 0.16 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | x former |  |  | 0.02 | 10 | 0.2
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | Calculation |  |  | 0.716 |  | 0.868 | 1.2123 | 0.545 | 0.47306 | 157.52 | 190.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 0.844 | 1.1921 | 0.545 | 0.45998 | 155.76 | 185.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 0.844 | 1.1921 | 0.545 | 0.45998 | 155.76 | 185.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 0.772 | 0.9602 | 0.5 | 0.386 | 160.8 | 154.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 0.844 | 1.0498 | 0.5 | 0.422 | 160.8 | 168.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 0.844 | 1.0498 | 0.415 | 0.35026 | 8.04 | 8.44
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 0.772 | 0.9602 | 0.415 | 0.32038 | 8.04 | 7.72
[11 empty] | Total | 2.8717 | 806.72 | 901.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 806.72 | total F
|  | 0.74696 | SAIFI=total F/total customers
|  | 0.83489 | SAIDI=total G/total customers
|  | 1.1177 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.5307e-05 | ASUI=1-ASAI
|  | 2871.66 | ENS=total ENS*1000
|  | 2.6589 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.545 | 2.9997 | 331.76 | 1210.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.545 | 2.9997 | 331.76 | 1210.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.545 | 2.9997 | 331.76 | 1210.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.5 | 2.752 | 301.6 | 1100.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.5 | 2.752 | 301.6 | 1100.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.415 | 2.2842 | 15.08 | 55.04
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.415 | 2.2842 | 15.08 | 55.04
[11 empty] | Total | 19.0714 | 1628.64 | 5944.32
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1628.64 | total F
|  | 1.508 | SAIFI=total F/total customers
|  | 5.504 | SAIDI=total G/total customers
|  | 3.6499 | CAIDI=SAIDI/SAIFI
|  | 0.99937 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00062831 | ASUI=1-ASAI
|  | 19071.36 | ENS=total ENS*1000
|  | 17.6587 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.716 |  | 2.288 | 3.1955 | 0.545 | 1.247 | 157.52 | 503.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 2.264 | 3.1977 | 0.545 | 1.2339 | 155.76 | 498.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 2.264 | 3.1977 | 0.545 | 1.2339 | 155.76 | 498.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 2.552 | 3.1741 | 0.5 | 1.276 | 160.8 | 510.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 2.552 | 3.1741 | 0.5 | 1.276 | 160.8 | 510.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 2.552 | 3.1741 | 0.415 | 1.0591 | 8.04 | 25.52
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 2.552 | 3.1741 | 0.415 | 1.0591 | 8.04 | 25.52
[11 empty] | Total | 8.3849 | 806.72 | 2571.36
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 806.72 | total F
|  | 0.74696 | SAIFI=total F/total customers
|  | 2.3809 | SAIDI=total G/total customers
|  | 3.1874 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00027179 | ASUI=1-ASAI
|  | 8384.88 | ENS=total ENS*1000
|  | 7.7638 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 1.264 | 0.8382 | 0.545 | 0.68888 | 331.76 | 278.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 1.244 | 0.82493 | 0.545 | 0.67798 | 331.76 | 273.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 1.674 | 1.1101 | 0.545 | 0.91233 | 331.76 | 368.28
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 1.674 | 1.1101 | 0.5 | 0.837 | 301.6 | 334.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 1.244 | 0.82493 | 0.5 | 0.622 | 301.6 | 248.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 1.674 | 1.1101 | 0.415 | 0.69471 | 15.08 | 16.74
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 1.674 | 1.1101 | 0.415 | 0.69471 | 15.08 | 16.74
[11 empty] | Total | 5.1276 | 1628.64 | 1537.12
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1628.64 | total F
|  | 1.508 | SAIFI=total F/total customers
|  | 1.4233 | SAIDI=total G/total customers
|  | 0.94381 | CAIDI=SAIDI/SAIFI
|  | 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00016247 | ASUI=1-ASAI
|  | 5127.61 | ENS=total ENS*1000
|  | 4.7478 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.716 |  | 0.868 | 1.2123 | 0.545 | 0.47306 | 157.52 | 190.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 0.844 | 1.1921 | 0.545 | 0.45998 | 155.76 | 185.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.708 |  | 0.844 | 1.1921 | 0.545 | 0.45998 | 155.76 | 185.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 0.772 | 0.9602 | 0.5 | 0.386 | 160.8 | 154.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 0.844 | 1.0498 | 0.5 | 0.422 | 160.8 | 168.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 0.844 | 1.0498 | 0.415 | 0.35026 | 8.04 | 8.44
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.804 |  | 0.772 | 0.9602 | 0.415 | 0.32038 | 8.04 | 7.72
[11 empty] | Total | 2.8717 | 806.72 | 901.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 806.72 | total F
|  | 0.74696 | SAIFI=total F/total customers
|  | 0.83489 | SAIDI=total G/total customers
|  | 1.1177 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.5307e-05 | ASUI=1-ASAI
|  | 2871.66 | ENS=total ENS*1000
|  | 2.6589 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 1.564 | 1.0371 | 0.545 | 0.85238 | 331.76 | 344.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 2.294 | 1.5212 | 0.545 | 1.2502 | 331.76 | 504.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 3.534 | 2.3435 | 0.545 | 1.926 | 331.76 | 777.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.508 |  | 3.534 | 2.3435 | 0.5 | 1.767 | 301.6 | 706.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 4.724 | 3.1326 | 0.5 | 2.362 | 301.6 | 944.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.415 | 2.2842 | 15.08 | 55.04
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.508 |  | 5.504 | 3.6499 | 0.415 | 2.2842 | 15.08 | 55.04
[11 empty] | Total | 12.726 | 1628.64 | 3387.92
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1628.64 | total F
|  | 1.508 | SAIFI=total F/total customers
|  | 3.137 | SAIDI=total G/total customers
|  | 2.0802 | CAIDI=SAIDI/SAIFI
|  | 0.99964 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0003581 | ASUI=1-ASAI
|  | 12725.96 | ENS=total ENS*1000
|  | 11.7833 | AENS=ENS/total customers

## F4_(18-25)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.02 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3359.52
0.02 | 0.16 | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 24412.88
0.02 | 0.16 |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 9454.72
0.02 | 0.16 |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 6560.13
0.02 | 0.16 |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 3359.52
0.02 | 0.16 |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 15850.08
0.02 | 0.16 |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
0.02 | 0.16 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | x former |  |  | 0.02 | 10 | 0.2
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.545 | 0.47088 | 164.56 | 190.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.792 | 1.0939 | 0.545 | 0.43164 | 159.28 | 174.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.545 | 0.47088 | 164.56 | 190.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.545 | 0.47088 | 164.56 | 190.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.792 | 1.0939 | 0.5 | 0.396 | 144.8 | 158.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.5 | 0.432 | 149.6 | 172.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.415 | 0.35856 | 7.48 | 8.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.792 | 1.0939 | 0.415 | 0.32868 | 7.24 | 7.92
[11 empty] | Total | 3.3595 | 962.08 | 1092.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 962.08 | total F
|  | 0.74006 | SAIFI=total F/total customers
|  | 0.84018 | SAIDI=total G/total customers
|  | 1.1353 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.5911e-05 | ASUI=1-ASAI
|  | 3359.52 | ENS=total ENS*1000
|  | 2.5842 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.545 | 3.318 | 364.32 | 1339.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.545 | 3.318 | 364.32 | 1339.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.545 | 3.318 | 364.32 | 1339.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.545 | 3.318 | 364.32 | 1339.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.5 | 3.044 | 331.2 | 1217.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.5 | 3.044 | 331.2 | 1217.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.415 | 2.5265 | 16.56 | 60.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.415 | 2.5265 | 16.56 | 60.88
[11 empty] | Total | 24.4129 | 2152.8 | 7914.4
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2152.8 | total F
|  | 1.656 | SAIFI=total F/total customers
|  | 6.088 | SAIDI=total G/total customers
|  | 3.6763 | CAIDI=SAIDI/SAIFI
|  | 0.99931 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00069498 | ASUI=1-ASAI
|  | 24412.88 | ENS=total ENS*1000
|  | 18.7791 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 2.384 | 3.1872 | 0.545 | 1.2993 | 164.56 | 524.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 2.312 | 3.1934 | 0.545 | 1.26 | 159.28 | 508.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 2.384 | 3.1872 | 0.545 | 1.2993 | 164.56 | 524.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 2.384 | 3.1872 | 0.545 | 1.2993 | 164.56 | 524.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 2.312 | 3.1934 | 0.5 | 1.156 | 144.8 | 462.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 2.384 | 3.1872 | 0.5 | 1.192 | 149.6 | 476.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 2.384 | 3.1872 | 0.415 | 0.98936 | 7.48 | 23.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 2.312 | 3.1934 | 0.415 | 0.95948 | 7.24 | 23.12
[11 empty] | Total | 9.4547 | 962.08 | 3068.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 962.08 | total F
|  | 0.74006 | SAIFI=total F/total customers
|  | 2.3602 | SAIDI=total G/total customers
|  | 3.1892 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026943 | ASUI=1-ASAI
|  | 9454.72 | ENS=total ENS*1000
|  | 7.2729 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.318 | 0.79589 | 0.545 | 0.71831 | 364.32 | 289.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.748 | 1.0556 | 0.545 | 0.95266 | 364.32 | 384.56
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.748 | 1.0556 | 0.545 | 0.95266 | 364.32 | 384.56
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.748 | 1.0556 | 0.545 | 0.95266 | 364.32 | 384.56
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.748 | 1.0556 | 0.5 | 0.874 | 331.2 | 349.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.318 | 0.79589 | 0.5 | 0.659 | 331.2 | 263.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.748 | 1.0556 | 0.415 | 0.72542 | 16.56 | 17.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.748 | 1.0556 | 0.415 | 0.72542 | 16.56 | 17.48
[11 empty] | Total | 6.5601 | 2152.8 | 2091.8
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2152.8 | total F
|  | 1.656 | SAIFI=total F/total customers
|  | 1.6091 | SAIDI=total G/total customers
|  | 0.97166 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00018368 | ASUI=1-ASAI
|  | 6560.13 | ENS=total ENS*1000
|  | 5.0463 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.545 | 0.47088 | 164.56 | 190.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.792 | 1.0939 | 0.545 | 0.43164 | 159.28 | 174.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.545 | 0.47088 | 164.56 | 190.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.545 | 0.47088 | 164.56 | 190.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.792 | 1.0939 | 0.5 | 0.396 | 144.8 | 158.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.5 | 0.432 | 149.6 | 172.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.748 |  | 0.864 | 1.1551 | 0.415 | 0.35856 | 7.48 | 8.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.792 | 1.0939 | 0.415 | 0.32868 | 7.24 | 7.92
[11 empty] | Total | 3.3595 | 962.08 | 1092.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 962.08 | total F
|  | 0.74006 | SAIFI=total F/total customers
|  | 0.84018 | SAIDI=total G/total customers
|  | 1.1353 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.5911e-05 | ASUI=1-ASAI
|  | 3359.52 | ENS=total ENS*1000
|  | 2.5842 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 1.638 | 0.98913 | 0.545 | 0.89271 | 364.32 | 360.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 2.878 | 1.7379 | 0.545 | 1.5685 | 364.32 | 633.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 2.878 | 1.7379 | 0.545 | 1.5685 | 364.32 | 633.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 4.118 | 2.4867 | 0.545 | 2.2443 | 364.32 | 905.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 4.118 | 2.4867 | 0.5 | 2.059 | 331.2 | 823.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.656 |  | 4.928 | 2.9758 | 0.5 | 2.464 | 331.2 | 985.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.415 | 2.5265 | 16.56 | 60.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.656 |  | 6.088 | 3.6763 | 0.415 | 2.5265 | 16.56 | 60.88
[11 empty] | Total | 15.8501 | 2152.8 | 4463.6
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2152.8 | total F
|  | 1.656 | SAIFI=total F/total customers
|  | 3.4335 | SAIDI=total G/total customers
|  | 2.0734 | CAIDI=SAIDI/SAIFI
|  | 0.99961 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00039196 | ASUI=1-ASAI
|  | 15850.08 | ENS=total ENS*1000
|  | 12.1924 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1548
0.16 | 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 6192
0.16 |  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 4128
0.16 |  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 1892
0.16 |  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36 | [5 empty] | E | 1548
0.16 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4552
0.16 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.464 |  | 0.532 | 1.1466 | 1 | 0.532 | 0.464 | 0.532
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.556 | 1.178 | 1 | 0.556 | 0.472 | 0.556
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 0.46 | 1.0455 | 1 | 0.46 | 0.44 | 0.46
[10 empty] | Total | 1.548 | 1.376 | 1.548
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 0.516 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.8904e-05 | ASUI=1-ASAI
| 1548 | ENS=total ENS*1000
| 516 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 6.192 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 6192 | ENS=total ENS*1000
| 2064 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.464 |  | 1.392 | 3 | 1 | 1.392 | 0.464 | 1.392
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 1.32 | 3 | 1 | 1.32 | 0.44 | 1.32
[10 empty] | Total | 4.128 | 1.376 | 4.128
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 1.376 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015708 | ASUI=1-ASAI
| 4128 | ENS=total ENS*1000
| 1376 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.664 | 0.96512 | 1 | 0.664 | 0.688 | 0.664
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
[10 empty] | Total | 1.892 | 2.064 | 1.892
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.63067 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.1994e-05 | ASUI=1-ASAI
| 1892 | ENS=total ENS*1000
| 630.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.964 | 1.4012 | 1 | 0.964 | 0.688 | 0.964
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.524 | 2.2151 | 1 | 1.524 | 0.688 | 1.524
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 4.552 | 2.064 | 4.552
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.5173 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017321 | ASUI=1-ASAI
| 4552 | ENS=total ENS*1000
| 1517.3333 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1738
0.16 | 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 7224
0.16 |  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 5028
0.16 |  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 2104
0.16 |  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1738
0.16 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5484
0.16 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1 | 0.476 | 0.472 | 0.476
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 0.548 | 1.1048 | 1 | 0.548 | 0.496 | 0.548
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1.5 | 0.714 | 0.472 | 0.476
[10 empty] | Total | 1.738 | 1.44 | 1.5
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 0.5 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.7078e-05 | ASUI=1-ASAI
| 1738 | ENS=total ENS*1000
| 579.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 7.224 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 7224 | ENS=total ENS*1000
| 2408 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 1.488 | 3 | 1 | 1.488 | 0.496 | 1.488
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
[10 empty] | Total | 5.028 | 1.44 | 4.32
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 1.44 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016438 | ASUI=1-ASAI
| 5028 | ENS=total ENS*1000
| 1676 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1.5 | 0.876 | 0.688 | 0.584
[10 empty] | Total | 2.104 | 2.064 | 1.812
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.604 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.895e-05 | ASUI=1-ASAI
| 2104 | ENS=total ENS*1000
| 701.3333 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.884 | 1.2849 | 1 | 0.884 | 0.688 | 0.884
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.504 | 2.186 | 1 | 1.504 | 0.688 | 1.504
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 5.484 | 2.064 | 4.452
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.484 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016941 | ASUI=1-ASAI
| 5484 | ENS=total ENS*1000
| 1828 | AENS=ENS/total customers

## F7_(32-38)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.02 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 2994.68
0.02 | 0.16 | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 19873.16
0.02 | 0.16 |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 8823.8
0.02 | 0.16 |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 5380.61
0.02 | 0.16 |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 2994.68
0.02 | 0.16 |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | F | 13198.21
0.02 | 0.16 |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.02 | 0.16 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.02 | 0.16 |  |  | x former |  |  | 0.02 | 10 | 0.2
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.02 | 0.16 |  |  | Calculation |  |  | 0.724 |  | 0.872 | 1.2044 | 0.545 | 0.47524 | 159.28 | 191.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.872 | 1.2044 | 0.545 | 0.47524 | 159.28 | 191.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.692 |  | 0.776 | 1.1214 | 0.545 | 0.42292 | 152.24 | 170.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 0.872 | 1.0634 | 0.545 | 0.47524 | 180.4 | 191.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 0.776 | 0.94634 | 0.5 | 0.388 | 164 | 155.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 0.872 | 1.0634 | 0.5 | 0.436 | 164 | 174.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 0.776 | 0.94634 | 0.415 | 0.32204 | 8.2 | 7.76
[11 empty] | Total | 2.9947 | 987.4 | 1083.6
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 987.4 | total F
|  | 0.76543 | SAIFI=total F/total customers
|  | 0.84 | SAIDI=total G/total customers
|  | 1.0974 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.589e-05 | ASUI=1-ASAI
|  | 2994.68 | ENS=total ENS*1000
|  | 2.3215 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.545 | 3.0128 | 333.52 | 1216.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.545 | 3.0128 | 333.52 | 1216.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.545 | 3.0128 | 333.52 | 1216.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.545 | 3.0128 | 333.52 | 1216.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.5 | 2.764 | 303.2 | 1105.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.5 | 2.764 | 303.2 | 1105.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.415 | 2.2941 | 15.16 | 55.28
[11 empty] | Total | 19.8732 | 1955.64 | 7131.12
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1955.64 | total F
|  | 1.516 | SAIFI=total F/total customers
|  | 5.528 | SAIDI=total G/total customers
|  | 3.6464 | CAIDI=SAIDI/SAIFI
|  | 0.99937 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00063105 | ASUI=1-ASAI
|  | 19873.16 | ENS=total ENS*1000
|  | 15.4056 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 2.312 | 3.1934 | 0.545 | 1.26 | 159.28 | 508.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 2.312 | 3.1934 | 0.545 | 1.26 | 159.28 | 508.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.692 |  | 2.216 | 3.2023 | 0.545 | 1.2077 | 152.24 | 487.52
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 2.6 | 3.1707 | 0.545 | 1.417 | 180.4 | 572
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 2.6 | 3.1707 | 0.5 | 1.3 | 164 | 520
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 2.6 | 3.1707 | 0.5 | 1.3 | 164 | 520
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 2.6 | 3.1707 | 0.415 | 1.079 | 8.2 | 26
[11 empty] | Total | 8.8238 | 987.4 | 3142.8
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 987.4 | total F
|  | 0.76543 | SAIFI=total F/total customers
|  | 2.4363 | SAIDI=total G/total customers
|  | 3.1829 | CAIDI=SAIDI/SAIFI
|  | 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00027811 | ASUI=1-ASAI
|  | 8823.8 | ENS=total ENS*1000
|  | 6.8402 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 1.268 | 0.83641 | 0.545 | 0.69106 | 333.52 | 278.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 1.268 | 0.83641 | 0.545 | 0.69106 | 333.52 | 278.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 1.698 | 1.1201 | 0.545 | 0.92541 | 333.52 | 373.56
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 1.698 | 1.1201 | 0.545 | 0.92541 | 333.52 | 373.56
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 1.188 | 0.78364 | 0.5 | 0.594 | 303.2 | 237.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 1.698 | 1.1201 | 0.5 | 0.849 | 303.2 | 339.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 1.698 | 1.1201 | 0.415 | 0.70467 | 15.16 | 16.98
[11 empty] | Total | 5.3806 | 1955.64 | 1899.22
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1955.64 | total F
|  | 1.516 | SAIFI=total F/total customers
|  | 1.4723 | SAIDI=total G/total customers
|  | 0.97115 | CAIDI=SAIDI/SAIFI
|  | 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00016807 | ASUI=1-ASAI
|  | 5380.61 | ENS=total ENS*1000
|  | 4.171 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.872 | 1.2044 | 0.545 | 0.47524 | 159.28 | 191.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.724 |  | 0.872 | 1.2044 | 0.545 | 0.47524 | 159.28 | 191.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.692 |  | 0.776 | 1.1214 | 0.545 | 0.42292 | 152.24 | 170.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 0.872 | 1.0634 | 0.545 | 0.47524 | 180.4 | 191.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 0.776 | 0.94634 | 0.5 | 0.388 | 164 | 155.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 0.872 | 1.0634 | 0.5 | 0.436 | 164 | 174.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.82 |  | 0.776 | 0.94634 | 0.415 | 0.32204 | 8.2 | 7.76
[11 empty] | Total | 2.9947 | 987.4 | 1083.6
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 987.4 | total F
|  | 0.76543 | SAIFI=total F/total customers
|  | 0.84 | SAIDI=total G/total customers
|  | 1.0974 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 9.589e-05 | ASUI=1-ASAI
|  | 2994.68 | ENS=total ENS*1000
|  | 2.3215 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 1.568 | 1.0343 | 0.545 | 0.85456 | 333.52 | 344.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 2.318 | 1.529 | 0.545 | 1.2633 | 333.52 | 509.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 3.558 | 2.347 | 0.545 | 1.9391 | 333.52 | 782.76
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 3.558 | 2.347 | 0.545 | 1.9391 | 333.52 | 782.76
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | x former |  |  | 0.02 | 0.5 | 0.01
|  |  |  | Calculation |  |  | 1.516 |  | 4.288 | 2.8285 | 0.5 | 2.144 | 303.2 | 857.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.5 | 2.764 | 303.2 | 1105.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | x former |  |  | 0.02 | 10 | 0.2
|  |  |  | Calculation |  |  | 1.516 |  | 5.528 | 3.6464 | 0.415 | 2.2941 | 15.16 | 55.28
[11 empty] | Total | 13.1982 | 1955.64 | 4438.92
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 1955.64 | total F
|  | 1.516 | SAIFI=total F/total customers
|  | 3.441 | SAIDI=total G/total customers
|  | 2.2698 | CAIDI=SAIDI/SAIFI
|  | 0.99961 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00039281 | ASUI=1-ASAI
|  | 13198.21 | ENS=total ENS*1000
|  | 10.2312 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 2949.12 | 1100 | 19656 | 1100 | 8143.92 | 1100 | 5313.45 | 1100 | 2949.12 | 1100 | 12948.35 | 1100
Feeder 2 | 1828 | 3 | 7308 | 3 | 4908 | 3 | 2228 | 3 | 1828 | 3 | 5288 | 3
Feeder 3 | 2871.66 | 1080 | 19071.36 | 1080 | 8384.88 | 1080 | 5127.61 | 1080 | 2871.66 | 1080 | 12725.96 | 1080
Feeder 4 | 3359.52 | 1300 | 24412.88 | 1300 | 9454.72 | 1300 | 6560.13 | 1300 | 3359.52 | 1300 | 15850.08 | 1300
Feeder 5 | 1548 | 3 | 6192 | 3 | 4128 | 3 | 1892 | 3 | 1548 | 3 | 4552 | 3
Feeder 6 | 1738 | 3 | 7224 | 3 | 5028 | 3 | 2104 | 3 | 1738 | 3 | 5484 | 3
Feeder 7 | 2994.68 | 1290 | 19873.16 | 1290 | 8823.8 | 1290 | 5380.61 | 1290 | 2994.68 | 1290 | 13198.21 | 1290
TOTAL | 17288.98 | 4779 | 103737.4 | 4779 | 48871.32 | 4779 | 28605.8 | 4779 | 17288.98 | 4779 | 70046.6 | 4779
Analytic | 17.289 |  | 103.7374 |  | 48.8713 |  | 28.6058 |  | 17.289 |  | 70.0466
Monte Carlo_Code | 17.287 |  | 103.73 |  | 47.645 |  | 28.604 |  | 17.287 |  | 69.905
Deviation | 0.011452 |  | 0.0071334 |  | 2.5093 |  | 0.0062924 |  | 0.011452 |  | 0.20215
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 17.292 | 17.28 | 17.297 | 17.287 |  | 945000 | 103.74 | 103.7 | 103.73 | 103.81
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 47.645 | 47.631 | 47.61 | 47.607 |  | 47500 | 28.607 | 28.602 | 28.604 | 28.591
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 17.287 | 17.295 | 17.29 | 17.292 |  | 1140000 | 69.905 | 69.816 | 69.896 | 69.832