## F1_(1-7)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.025 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3124.62
0.025 | 0.16 | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 20884.5
0.025 | 0.16 |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 8319.42
0.025 | 0.16 |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 5630.6625
0.025 | 0.16 |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 3124.62
0.025 | 0.16 |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 13689.2625
0.025 | 0.16 |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
0.025 | 0.16 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | x former |  |  | 0.025 | 10 | 0.25
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | Calculation |  |  | 0.713 |  | 0.834 | 1.1697 | 0.545 | 0.45453 | 156.86 | 183.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.737 |  | 0.906 | 1.2293 | 0.545 | 0.49377 | 162.14 | 199.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 0.834 | 1.1697 | 0.545 | 0.45453 | 156.86 | 183.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 0.93 | 1.0751 | 0.545 | 0.50685 | 190.3 | 204.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 0.906 | 1.0474 | 0.5 | 0.453 | 173 | 181.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 0.93 | 1.0751 | 0.415 | 0.38595 | 8.65 | 9.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 0.906 | 1.0474 | 0.415 | 0.37599 | 8.65 | 9.06
[11 empty] | Total | 3.1246 | 856.46 | 970.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 856.46 | total F
|  | 0.7786 | SAIFI=total F/total customers
|  | 0.88222 | SAIDI=total G/total customers
|  | 1.1331 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00010071 | ASUI=1-ASAI
|  | 3124.62 | ENS=total ENS*1000
|  | 2.8406 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.545 | 3.2428 | 346.5 | 1309
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.545 | 3.2428 | 346.5 | 1309
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.545 | 3.2428 | 346.5 | 1309
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.545 | 3.2428 | 346.5 | 1309
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.5 | 2.975 | 315 | 1190
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.415 | 2.4692 | 15.75 | 59.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.415 | 2.4692 | 15.75 | 59.5
[11 empty] | Total | 20.8845 | 1732.5 | 6545
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1732.5 | total F
|  | 1.575 | SAIFI=total F/total customers
|  | 5.95 | SAIDI=total G/total customers
|  | 3.7778 | CAIDI=SAIDI/SAIFI
|  | 0.99932 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00067922 | ASUI=1-ASAI
|  | 20884.5 | ENS=total ENS*1000
|  | 18.9859 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 2.314 | 3.2454 | 0.545 | 1.2611 | 156.86 | 509.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.737 |  | 2.386 | 3.2374 | 0.545 | 1.3004 | 162.14 | 524.92
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 2.314 | 3.2454 | 0.545 | 1.2611 | 156.86 | 509.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 2.41 | 2.7861 | 0.545 | 1.3135 | 190.3 | 530.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 2.386 | 2.7584 | 0.5 | 1.193 | 173 | 477.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 2.41 | 2.7861 | 0.415 | 1.0002 | 8.65 | 24.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 2.386 | 2.7584 | 0.415 | 0.99019 | 8.65 | 23.86
[11 empty] | Total | 8.3194 | 856.46 | 2598.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 856.46 | total F
|  | 0.7786 | SAIFI=total F/total customers
|  | 2.3622 | SAIDI=total G/total customers
|  | 3.0339 | CAIDI=SAIDI/SAIFI
|  | 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00026966 | ASUI=1-ASAI
|  | 8319.42 | ENS=total ENS*1000
|  | 7.5631 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 1.265 | 0.80317 | 0.545 | 0.68943 | 346.5 | 278.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 1.325 | 0.84127 | 0.545 | 0.72213 | 346.5 | 291.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 1.265 | 0.80317 | 0.545 | 0.68942 | 346.5 | 278.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 1.8825 | 1.1952 | 0.545 | 1.026 | 346.5 | 414.15
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 1.8825 | 1.1952 | 0.5 | 0.94125 | 315 | 376.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 1.8825 | 1.1952 | 0.415 | 0.78124 | 15.75 | 18.825
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 1.8825 | 1.1952 | 0.415 | 0.78124 | 15.75 | 18.825
[11 empty] | Total | 5.6307 | 1732.5 | 1676.4
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1732.5 | total F
|  | 1.575 | SAIFI=total F/total customers
|  | 1.524 | SAIDI=total G/total customers
|  | 0.96762 | CAIDI=SAIDI/SAIFI
|  | 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00017397 | ASUI=1-ASAI
|  | 5630.6625 | ENS=total ENS*1000
|  | 5.1188 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 0.834 | 1.1697 | 0.545 | 0.45453 | 156.86 | 183.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.737 |  | 0.906 | 1.2293 | 0.545 | 0.49377 | 162.14 | 199.32
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 0.834 | 1.1697 | 0.545 | 0.45453 | 156.86 | 183.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 0.93 | 1.0751 | 0.545 | 0.50685 | 190.3 | 204.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 0.906 | 1.0474 | 0.5 | 0.453 | 173 | 181.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 0.93 | 1.0751 | 0.415 | 0.38595 | 8.65 | 9.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.865 |  | 0.906 | 1.0474 | 0.415 | 0.37599 | 8.65 | 9.06
[11 empty] | Total | 3.1246 | 856.46 | 970.44
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 856.46 | total F
|  | 0.7786 | SAIFI=total F/total customers
|  | 0.88222 | SAIDI=total G/total customers
|  | 1.1331 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00010071 | ASUI=1-ASAI
|  | 3124.62 | ENS=total ENS*1000
|  | 2.8406 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 1 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 1.565 | 0.99365 | 0.545 | 0.85293 | 346.5 | 344.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 2 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 2.4225 | 1.5381 | 0.545 | 1.3203 | 346.5 | 532.95
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 3 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 3.22 | 2.0444 | 0.545 | 1.7549 | 346.5 | 708.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 4 | 220 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 4.615 | 2.9302 | 0.545 | 2.5152 | 346.5 | 1015.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 5 | 200 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.575 |  | 4.615 | 2.9302 | 0.5 | 2.3075 | 315 | 923
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 6 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.415 | 2.4692 | 15.75 | 59.5
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 7 | 10 | 1 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 3 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 5 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 7 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 10 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 2 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 4 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 6 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 8 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 9 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 11 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 12 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.575 |  | 5.95 | 3.7778 | 0.415 | 2.4692 | 15.75 | 59.5
[11 empty] | Total | 13.6893 | 1732.5 | 3642.95
|  | 1100 | total customers
|  | 9636000 | total (customers*8760)
|  | 1732.5 | total F
|  | 1.575 | SAIFI=total F/total customers
|  | 3.3118 | SAIDI=total G/total customers
|  | 2.1027 | CAIDI=SAIDI/SAIFI
|  | 0.99962 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00037806 | ASUI=1-ASAI
|  | 13689.2625 | ENS=total ENS*1000
|  | 12.4448 | AENS=ENS/total customers

## F2_(8-10)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1828
0.16 | 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 7308
0.16 |  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 4908
0.16 |  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | D | 2228
0.16 |  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1828
0.16 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5288
0.16 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.448 |  | 0.464 | 1.0357 | 1 | 0.464 | 0.448 | 0.464
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.536 | 1.1356 | 1.5 | 0.804 | 0.472 | 0.536
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 0.56 | 1.1667 | 1 | 0.56 | 0.48 | 0.56
[10 empty] | Total | 1.828 | 1.4 | 1.56
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 0.52 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.9361e-05 | ASUI=1-ASAI
| 1828 | ENS=total ENS*1000
| 609.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1.5 | 3.132 | 0.696 | 2.088
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 7.308 | 2.088 | 6.264
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 2.088 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023836 | ASUI=1-ASAI
| 7308 | ENS=total ENS*1000
| 2436 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.448 |  | 1.344 | 3 | 1 | 1.344 | 0.448 | 1.344
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.48 |  | 1.44 | 3 | 1 | 1.44 | 0.48 | 1.44
[10 empty] | Total | 4.908 | 1.4 | 4.2
| 3 | total customers
| 26280 | total (customers*8760)
| 1.4 | total F
| 0.46667 | SAIFI=total F/total customers
| 1.4 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015982 | ASUI=1-ASAI
| 4908 | ENS=total ENS*1000
| 1636 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.588 | 0.84483 | 1 | 0.588 | 0.696 | 0.588
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.648 | 0.93103 | 1.5 | 0.972 | 0.696 | 0.648
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 0.668 | 0.95977 | 1 | 0.668 | 0.696 | 0.668
[10 empty] | Total | 2.228 | 2.088 | 1.904
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 0.63467 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.2451e-05 | ASUI=1-ASAI
| 2228 | ENS=total ENS*1000
| 742.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 0.908 | 1.3046 | 1 | 0.908 | 0.696 | 0.908
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | Calculation |  |  | 0.696 |  | 1.528 | 2.1954 | 1.5 | 2.292 | 0.696 | 1.528
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 15 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 17 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 14 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 16 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 18 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | Calculation |  |  | 0.696 |  | 2.088 | 3 | 1 | 2.088 | 0.696 | 2.088
[10 empty] | Total | 5.288 | 2.088 | 4.524
| 3 | total customers
| 26280 | total (customers*8760)
| 2.088 | total F
| 0.696 | SAIFI=total F/total customers
| 1.508 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017215 | ASUI=1-ASAI
| 5288 | ENS=total ENS*1000
| 1762.6667 | AENS=ENS/total customers

## F3_(11-17)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.025 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3044.91
0.025 | 0.16 | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 20284.11
0.025 | 0.16 |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 8558.13
0.025 | 0.16 |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 5441.8975
0.025 | 0.16 |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 3044.91
0.025 | 0.16 |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 13505.035
0.025 | 0.16 |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.025 | 0.16 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | x former |  |  | 0.025 | 10 | 0.25
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | Calculation |  |  | 0.721 |  | 0.918 | 1.2732 | 0.545 | 0.50031 | 158.62 | 201.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 0.894 | 1.2539 | 0.545 | 0.48723 | 156.86 | 196.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 0.894 | 1.2539 | 0.545 | 0.48723 | 156.86 | 196.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 0.822 | 1.0161 | 0.5 | 0.411 | 161.8 | 164.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 0.894 | 1.1051 | 0.5 | 0.447 | 161.8 | 178.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 0.894 | 1.1051 | 0.415 | 0.37101 | 8.09 | 8.94
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 0.822 | 1.0161 | 0.415 | 0.34113 | 8.09 | 8.22
[11 empty] | Total | 3.0449 | 812.12 | 955.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 812.12 | total F
|  | 0.75196 | SAIFI=total F/total customers
|  | 0.88489 | SAIDI=total G/total customers
|  | 1.1768 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00010101 | ASUI=1-ASAI
|  | 3044.91 | ENS=total ENS*1000
|  | 2.8194 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.545 | 3.1904 | 339.46 | 1287.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.545 | 3.1904 | 339.46 | 1287.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.545 | 3.1904 | 339.46 | 1287.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.5 | 2.927 | 308.6 | 1170.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.5 | 2.927 | 308.6 | 1170.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.415 | 2.4294 | 15.43 | 58.54
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.415 | 2.4294 | 15.43 | 58.54
[11 empty] | Total | 20.2841 | 1666.44 | 6322.32
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1666.44 | total F
|  | 1.543 | SAIFI=total F/total customers
|  | 5.854 | SAIDI=total G/total customers
|  | 3.7939 | CAIDI=SAIDI/SAIFI
|  | 0.99933 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00066826 | ASUI=1-ASAI
|  | 20284.11 | ENS=total ENS*1000
|  | 18.7816 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.721 |  | 2.338 | 3.2427 | 0.545 | 1.2742 | 158.62 | 514.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 2.314 | 3.2454 | 0.545 | 1.2611 | 156.86 | 509.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 2.314 | 3.2454 | 0.545 | 1.2611 | 156.86 | 509.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 2.602 | 3.2163 | 0.5 | 1.301 | 161.8 | 520.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 2.602 | 3.2163 | 0.5 | 1.301 | 161.8 | 520.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 2.602 | 3.2163 | 0.415 | 1.0798 | 8.09 | 26.02
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 2.602 | 3.2163 | 0.415 | 1.0798 | 8.09 | 26.02
[11 empty] | Total | 8.5581 | 812.12 | 2625.36
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 812.12 | total F
|  | 0.75196 | SAIFI=total F/total customers
|  | 2.4309 | SAIDI=total G/total customers
|  | 3.2327 | CAIDI=SAIDI/SAIFI
|  | 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0002775 | ASUI=1-ASAI
|  | 8558.13 | ENS=total ENS*1000
|  | 7.9242 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 1.329 | 0.86131 | 0.545 | 0.7243 | 339.46 | 292.38
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 1.309 | 0.84835 | 0.545 | 0.71341 | 339.46 | 287.98
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 1.7865 | 1.1578 | 0.545 | 0.97364 | 339.46 | 393.03
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 1.7865 | 1.1578 | 0.5 | 0.89325 | 308.6 | 357.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 1.309 | 0.84835 | 0.5 | 0.6545 | 308.6 | 261.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 1.7865 | 1.1578 | 0.415 | 0.7414 | 15.43 | 17.865
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 1.7865 | 1.1578 | 0.415 | 0.7414 | 15.43 | 17.865
[11 empty] | Total | 5.4419 | 1666.44 | 1628.22
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1666.44 | total F
|  | 1.543 | SAIFI=total F/total customers
|  | 1.5076 | SAIDI=total G/total customers
|  | 0.97706 | CAIDI=SAIDI/SAIFI
|  | 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0001721 | ASUI=1-ASAI
|  | 5441.8975 | ENS=total ENS*1000
|  | 5.0388 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.721 |  | 0.918 | 1.2732 | 0.545 | 0.50031 | 158.62 | 201.96
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 0.894 | 1.2539 | 0.545 | 0.48723 | 156.86 | 196.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.713 |  | 0.894 | 1.2539 | 0.545 | 0.48723 | 156.86 | 196.68
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 0.822 | 1.0161 | 0.5 | 0.411 | 161.8 | 164.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 0.894 | 1.1051 | 0.5 | 0.447 | 161.8 | 178.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 0.894 | 1.1051 | 0.415 | 0.37101 | 8.09 | 8.94
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0 | 0
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.809 |  | 0.822 | 1.0161 | 0.415 | 0.34113 | 8.09 | 8.22
[11 empty] | Total | 3.0449 | 812.12 | 955.68
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 812.12 | total F
|  | 0.75196 | SAIFI=total F/total customers
|  | 0.88489 | SAIDI=total G/total customers
|  | 1.1768 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00010101 | ASUI=1-ASAI
|  | 3044.91 | ENS=total ENS*1000
|  | 2.8194 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 11 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 1.629 | 1.0557 | 0.545 | 0.88781 | 339.46 | 358.38
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 12 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 2.4065 | 1.5596 | 0.545 | 1.3115 | 339.46 | 529.43
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 13 | 220 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 3.7415 | 2.4248 | 0.545 | 2.0391 | 339.46 | 823.13
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 14 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.543 |  | 3.7415 | 2.4248 | 0.5 | 1.8708 | 308.6 | 748.3
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 15 | 200 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.074 | 3.2884 | 0.5 | 2.537 | 308.6 | 1014.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 16 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.415 | 2.4294 | 15.43 | 58.54
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 17 | 10 | 19 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 21 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 23 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 26 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 28 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 20 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 22 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 24 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 25 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 27 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 29 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 30 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.543 |  | 5.854 | 3.7939 | 0.415 | 2.4294 | 15.43 | 58.54
[11 empty] | Total | 13.505 | 1666.44 | 3591.12
|  | 1080 | total customers
|  | 9460800 | total (customers*8760)
|  | 1666.44 | total F
|  | 1.543 | SAIFI=total F/total customers
|  | 3.3251 | SAIDI=total G/total customers
|  | 2.155 | CAIDI=SAIDI/SAIFI
|  | 0.99962 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00037958 | ASUI=1-ASAI
|  | 13505.035 | ENS=total ENS*1000
|  | 12.5047 | AENS=ENS/total customers

## F4_(18-25)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.025 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3560.02
0.025 | 0.16 | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 26016.88
0.025 | 0.16 |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 9655.22
0.025 | 0.16 |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 6971.6425
0.025 | 0.16 |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | E | 3560.02
0.025 | 0.16 |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | F | 16817.58
0.025 | 0.16 |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
0.025 | 0.16 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | x former |  |  | 0.025 | 10 | 0.25
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | x former |  |  | 0 | 0 | 0
| 0.16 |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.545 | 0.49813 | 165.66 | 201.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.842 | 1.155 | 0.545 | 0.45889 | 160.38 | 185.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.545 | 0.49813 | 165.66 | 201.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.545 | 0.49813 | 165.66 | 201.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.842 | 1.155 | 0.5 | 0.421 | 145.8 | 168.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.5 | 0.457 | 150.6 | 182.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.415 | 0.37931 | 7.53 | 9.14
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.842 | 1.155 | 0.415 | 0.34943 | 7.29 | 8.42
[11 empty] | Total | 3.56 | 968.58 | 1157.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 968.58 | total F
|  | 0.74506 | SAIFI=total F/total customers
|  | 0.89018 | SAIDI=total G/total customers
|  | 1.1948 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00010162 | ASUI=1-ASAI
|  | 3560.02 | ENS=total ENS*1000
|  | 2.7385 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.545 | 3.536 | 373.12 | 1427.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.545 | 3.536 | 373.12 | 1427.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.545 | 3.536 | 373.12 | 1427.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.545 | 3.536 | 373.12 | 1427.36
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.5 | 3.244 | 339.2 | 1297.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.5 | 3.244 | 339.2 | 1297.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.415 | 2.6925 | 16.96 | 64.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.415 | 2.6925 | 16.96 | 64.88
[11 empty] | Total | 26.0169 | 2204.8 | 8434.4
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2204.8 | total F
|  | 1.696 | SAIFI=total F/total customers
|  | 6.488 | SAIDI=total G/total customers
|  | 3.8255 | CAIDI=SAIDI/SAIFI
|  | 0.99926 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00074064 | ASUI=1-ASAI
|  | 26016.88 | ENS=total ENS*1000
|  | 20.013 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 2.434 | 3.2324 | 0.545 | 1.3265 | 165.66 | 535.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 2.362 | 3.2401 | 0.545 | 1.2873 | 160.38 | 519.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 2.434 | 3.2324 | 0.545 | 1.3265 | 165.66 | 535.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 2.434 | 3.2324 | 0.545 | 1.3265 | 165.66 | 535.48
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 2.362 | 3.2401 | 0.5 | 1.181 | 145.8 | 472.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 2.434 | 3.2324 | 0.5 | 1.217 | 150.6 | 486.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 2.434 | 3.2324 | 0.415 | 1.0101 | 7.53 | 24.34
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 2.362 | 3.2401 | 0.415 | 0.98023 | 7.29 | 23.62
[11 empty] | Total | 9.6552 | 968.58 | 3133.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 968.58 | total F
|  | 0.74506 | SAIFI=total F/total customers
|  | 2.4102 | SAIDI=total G/total customers
|  | 3.2349 | CAIDI=SAIDI/SAIFI
|  | 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00027514 | ASUI=1-ASAI
|  | 9655.22 | ENS=total ENS*1000
|  | 7.4271 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.3855 | 0.81692 | 0.545 | 0.7551 | 373.12 | 304.81
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.863 | 1.0985 | 0.545 | 1.0153 | 373.12 | 409.86
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.863 | 1.0985 | 0.545 | 1.0153 | 373.12 | 409.86
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.863 | 1.0985 | 0.545 | 1.0153 | 373.12 | 409.86
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.863 | 1.0985 | 0.5 | 0.9315 | 339.2 | 372.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.3855 | 0.81692 | 0.5 | 0.69275 | 339.2 | 277.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.863 | 1.0985 | 0.415 | 0.77314 | 16.96 | 18.63
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.863 | 1.0985 | 0.415 | 0.77314 | 16.96 | 18.63
[11 empty] | Total | 6.9716 | 2204.8 | 2221.35
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2204.8 | total F
|  | 1.696 | SAIFI=total F/total customers
|  | 1.7087 | SAIDI=total G/total customers
|  | 1.0075 | CAIDI=SAIDI/SAIFI
|  | 0.9998 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00019506 | ASUI=1-ASAI
|  | 6971.6425 | ENS=total ENS*1000
|  | 5.3628 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.545 | 0.49813 | 165.66 | 201.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.842 | 1.155 | 0.545 | 0.45889 | 160.38 | 185.24
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.545 | 0.49813 | 165.66 | 201.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.545 | 0.49813 | 165.66 | 201.08
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.842 | 1.155 | 0.5 | 0.421 | 145.8 | 168.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.5 | 0.457 | 150.6 | 182.8
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.753 |  | 0.914 | 1.2138 | 0.415 | 0.37931 | 7.53 | 9.14
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.842 | 1.155 | 0.415 | 0.34943 | 7.29 | 8.42
[11 empty] | Total | 3.56 | 968.58 | 1157.24
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 968.58 | total F
|  | 0.74506 | SAIFI=total F/total customers
|  | 0.89018 | SAIDI=total G/total customers
|  | 1.1948 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00010162 | ASUI=1-ASAI
|  | 3560.02 | ENS=total ENS*1000
|  | 2.7385 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 18 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 1.7055 | 1.0056 | 0.545 | 0.9295 | 373.12 | 375.21
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 19 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 3.0405 | 1.7927 | 0.545 | 1.6571 | 373.12 | 668.91
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 20 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 3.0405 | 1.7927 | 0.545 | 1.6571 | 373.12 | 668.91
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 21 | 220 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 4.3755 | 2.5799 | 0.545 | 2.3846 | 373.12 | 962.61
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 22 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 4.3755 | 2.5799 | 0.5 | 2.1878 | 339.2 | 875.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 23 | 200 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.696 |  | 5.233 | 3.0855 | 0.5 | 2.6165 | 339.2 | 1046.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 24 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.415 | 2.6925 | 16.96 | 64.88
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 25 | 10 | 31 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 33 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 36 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 39 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 41 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 32 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 34 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 35 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 37 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 38 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 40 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 42 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 43 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.696 |  | 6.488 | 3.8255 | 0.415 | 2.6925 | 16.96 | 64.88
[11 empty] | Total | 16.8176 | 2204.8 | 4727.1
|  | 1300 | total customers
|  | 11388000 | total (customers*8760)
|  | 2204.8 | total F
|  | 1.696 | SAIFI=total F/total customers
|  | 3.6362 | SAIDI=total G/total customers
|  | 2.144 | CAIDI=SAIDI/SAIFI
|  | 0.99958 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00041509 | ASUI=1-ASAI
|  | 16817.58 | ENS=total ENS*1000
|  | 12.9366 | AENS=ENS/total customers

## F5_(26-28)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1548
0.16 | 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | B | 6192
0.16 |  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 4128
0.16 |  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 1892
0.16 |  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36 | [5 empty] | E | 1548
0.16 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4552
0.16 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.464 |  | 0.532 | 1.1466 | 1 | 0.532 | 0.464 | 0.532
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 0.556 | 1.178 | 1 | 0.556 | 0.472 | 0.556
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 0.46 | 1.0455 | 1 | 0.46 | 0.44 | 0.46
[10 empty] | Total | 1.548 | 1.376 | 1.548
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 0.516 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.8904e-05 | ASUI=1-ASAI
| 1548 | ENS=total ENS*1000
| 516 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 6.192 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 6192 | ENS=total ENS*1000
| 2064 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.464 |  | 1.392 | 3 | 1 | 1.392 | 0.464 | 1.392
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.44 |  | 1.32 | 3 | 1 | 1.32 | 0.44 | 1.32
[10 empty] | Total | 4.128 | 1.376 | 4.128
| 3 | total customers
| 26280 | total (customers*8760)
| 1.376 | total F
| 0.45867 | SAIFI=total F/total customers
| 1.376 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015708 | ASUI=1-ASAI
| 4128 | ENS=total ENS*1000
| 1376 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.664 | 0.96512 | 1 | 0.664 | 0.688 | 0.664
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
[10 empty] | Total | 1.892 | 2.064 | 1.892
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.63067 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.1994e-05 | ASUI=1-ASAI
| 1892 | ENS=total ENS*1000
| 630.6667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.964 | 1.4012 | 1 | 0.964 | 0.688 | 0.964
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.524 | 2.2151 | 1 | 1.524 | 0.688 | 1.524
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 46 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 48 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 45 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 47 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 49 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
[10 empty] | Total | 4.552 | 2.064 | 4.552
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.5173 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00017321 | ASUI=1-ASAI
| 4552 | ENS=total ENS*1000
| 1517.3333 | AENS=ENS/total customers

## F6_(29-31)
Lfr | [6 empty] | CASE A & E | [6 empty] | ENS
0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1738
0.16 | 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 7224
0.16 |  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | C | 5028
0.16 |  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064 | [5 empty] | D | 2104
0.16 |  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288 | [5 empty] | E | 1738
0.16 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5484
0.16 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.16 |  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1 | 0.476 | 0.472 | 0.476
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 0.548 | 1.1048 | 1 | 0.548 | 0.496 | 0.548
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 0.476 | 1.0085 | 1.5 | 0.714 | 0.472 | 0.476
[10 empty] | Total | 1.738 | 1.44 | 1.5
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 0.5 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.7078e-05 | ASUI=1-ASAI
| 1738 | ENS=total ENS*1000
| 579.3333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1 | 2.064 | 0.688 | 2.064
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 7.224 | 2.064 | 6.192
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 2.064 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023562 | ASUI=1-ASAI
| 7224 | ENS=total ENS*1000
| 2408 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1 | 1.416 | 0.472 | 1.416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.496 |  | 1.488 | 3 | 1 | 1.488 | 0.496 | 1.488
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.472 |  | 1.416 | 3 | 1.5 | 2.124 | 0.472 | 1.416
[10 empty] | Total | 5.028 | 1.44 | 4.32
| 3 | total customers
| 26280 | total (customers*8760)
| 1.44 | total F
| 0.48 | SAIFI=total F/total customers
| 1.44 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016438 | ASUI=1-ASAI
| 5028 | ENS=total ENS*1000
| 1676 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1 | 0.584 | 0.688 | 0.584
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.644 | 0.93605 | 1 | 0.644 | 0.688 | 0.644
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 0.584 | 0.84884 | 1.5 | 0.876 | 0.688 | 0.584
[10 empty] | Total | 2.104 | 2.064 | 1.812
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 0.604 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.895e-05 | ASUI=1-ASAI
| 2104 | ENS=total ENS*1000
| 701.3333 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 0.884 | 1.2849 | 1 | 0.884 | 0.688 | 0.884
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  | Calculation |  |  | 0.688 |  | 1.504 | 2.186 | 1 | 1.504 | 0.688 | 1.504
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 52 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 54 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  | 51 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | 53 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  | 55 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  | Calculation |  |  | 0.688 |  | 2.064 | 3 | 1.5 | 3.096 | 0.688 | 2.064
[10 empty] | Total | 5.484 | 2.064 | 4.452
| 3 | total customers
| 26280 | total (customers*8760)
| 2.064 | total F
| 0.688 | SAIFI=total F/total customers
| 1.484 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99983 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016941 | ASUI=1-ASAI
| 5484 | ENS=total ENS*1000
| 1828 | AENS=ENS/total customers

## F7_(32-38)
Tfr | Lfr | [6 empty] | CASE A | [6 empty] | ENS
0.025 | 0.16 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 3174.43
0.025 | 0.16 | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 21131.41
0.025 | 0.16 |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048 | [5 empty] | C | 9003.55
0.025 | 0.16 |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 5709.5225
0.025 | 0.16 |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 3174.43
0.025 | 0.16 |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06 | [5 empty] | F | 13968.8725
0.025 | 0.16 |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
0.025 | 0.16 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.025 | 0.16 |  |  | x former |  |  | 0.025 | 10 | 0.25
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | x former |  |  | 0 | 0 | 0
0.025 | 0.16 |  |  | Calculation |  |  | 0.729 |  | 0.922 | 1.2647 | 0.545 | 0.50249 | 160.38 | 202.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.922 | 1.2647 | 0.545 | 0.50249 | 160.38 | 202.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.697 |  | 0.826 | 1.1851 | 0.545 | 0.45017 | 153.34 | 181.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 0.922 | 1.1176 | 0.545 | 0.50249 | 181.5 | 202.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 0.826 | 1.0012 | 0.5 | 0.413 | 165 | 165.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 0.922 | 1.1176 | 0.5 | 0.461 | 165 | 184.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 0.826 | 1.0012 | 0.415 | 0.34279 | 8.25 | 8.26
[11 empty] | Total | 3.1744 | 993.85 | 1148.1
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 993.85 | total F
|  | 0.77043 | SAIFI=total F/total customers
|  | 0.89 | SAIDI=total G/total customers
|  | 1.1552 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0001016 | ASUI=1-ASAI
|  | 3174.43 | ENS=total ENS*1000
|  | 2.4608 | AENS=ENS/total customers
CASE B
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.545 | 3.2035 | 341.22 | 1293.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.545 | 3.2035 | 341.22 | 1293.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.545 | 3.2035 | 341.22 | 1293.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.545 | 3.2035 | 341.22 | 1293.16
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.5 | 2.939 | 310.2 | 1175.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.5 | 2.939 | 310.2 | 1175.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.415 | 2.4394 | 15.51 | 58.78
[11 empty] | Total | 21.1314 | 2000.79 | 7582.62
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 2000.79 | total F
|  | 1.551 | SAIFI=total F/total customers
|  | 5.878 | SAIDI=total G/total customers
|  | 3.7898 | CAIDI=SAIDI/SAIFI
|  | 0.99933 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.000671 | ASUI=1-ASAI
|  | 21131.41 | ENS=total ENS*1000
|  | 16.3809 | AENS=ENS/total customers
CASE C
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 2.362 | 3.2401 | 0.545 | 1.2873 | 160.38 | 519.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 2.362 | 3.2401 | 0.545 | 1.2873 | 160.38 | 519.64
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.697 |  | 2.266 | 3.2511 | 0.545 | 1.235 | 153.34 | 498.52
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 2.65 | 3.2121 | 0.545 | 1.4442 | 181.5 | 583
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 2.65 | 3.2121 | 0.5 | 1.325 | 165 | 530
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 2.65 | 3.2121 | 0.5 | 1.325 | 165 | 530
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 2.65 | 3.2121 | 0.415 | 1.0997 | 8.25 | 26.5
[11 empty] | Total | 9.0035 | 993.85 | 3207.3
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 993.85 | total F
|  | 0.77043 | SAIFI=total F/total customers
|  | 2.4863 | SAIDI=total G/total customers
|  | 3.2271 | CAIDI=SAIDI/SAIFI
|  | 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00028382 | ASUI=1-ASAI
|  | 9003.55 | ENS=total ENS*1000
|  | 6.9795 | AENS=ENS/total customers
CASE D
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 1.333 | 0.85945 | 0.545 | 0.72649 | 341.22 | 293.26
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 1.333 | 0.85945 | 0.545 | 0.72649 | 341.22 | 293.26
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 1.8105 | 1.1673 | 0.545 | 0.98672 | 341.22 | 398.31
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 1.8105 | 1.1673 | 0.545 | 0.98672 | 341.22 | 398.31
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 1.253 | 0.80787 | 0.5 | 0.6265 | 310.2 | 250.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 1.8105 | 1.1673 | 0.5 | 0.90525 | 310.2 | 362.1
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 1.8105 | 1.1673 | 0.415 | 0.75136 | 15.51 | 18.105
[11 empty] | Total | 5.7095 | 2000.79 | 2013.945
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 2000.79 | total F
|  | 1.551 | SAIFI=total F/total customers
|  | 1.5612 | SAIDI=total G/total customers
|  | 1.0066 | CAIDI=SAIDI/SAIFI
|  | 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00017822 | ASUI=1-ASAI
|  | 5709.5225 | ENS=total ENS*1000
|  | 4.426 | AENS=ENS/total customers
CASE E
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.922 | 1.2647 | 0.545 | 0.50249 | 160.38 | 202.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.729 |  | 0.922 | 1.2647 | 0.545 | 0.50249 | 160.38 | 202.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.697 |  | 0.826 | 1.1851 | 0.545 | 0.45017 | 153.34 | 181.72
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 0.922 | 1.1176 | 0.545 | 0.50249 | 181.5 | 202.84
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 0.826 | 1.0012 | 0.5 | 0.413 | 165 | 165.2
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0 | 0
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 0.922 | 1.1176 | 0.5 | 0.461 | 165 | 184.4
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0 | 0
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | x former |  |  | 0 | 0 | 0
|  |  |  | Calculation |  |  | 0.825 |  | 0.826 | 1.0012 | 0.415 | 0.34279 | 8.25 | 8.26
[11 empty] | Total | 3.1744 | 993.85 | 1148.1
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 993.85 | total F
|  | 0.77043 | SAIFI=total F/total customers
|  | 0.89 | SAIDI=total G/total customers
|  | 1.1552 | CAIDI=SAIDI/SAIFI
|  | 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.0001016 | ASUI=1-ASAI
|  | 3174.43 | ENS=total ENS*1000
|  | 2.4608 | AENS=ENS/total customers
CASE F
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 32 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 1.633 | 1.0529 | 0.545 | 0.88999 | 341.22 | 359.26
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 33 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 2.4305 | 1.5671 | 0.545 | 1.3246 | 341.22 | 534.71
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 34 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 3.7655 | 2.4278 | 0.545 | 2.0522 | 341.22 | 828.41
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 35 | 220 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 3.7655 | 2.4278 | 0.545 | 2.0522 | 341.22 | 828.41
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 36 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 0.5 | 0.06
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 0.5 | 0.064
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 0.5 | 0.048
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | x former |  |  | 0.025 | 0.5 | 0.0125
|  |  |  | Calculation |  |  | 1.551 |  | 4.543 | 2.9291 | 0.5 | 2.2715 | 310.2 | 908.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 37 | 200 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.5 | 2.939 | 310.2 | 1175.6
|  | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
|  | 38 | 10 | 56 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 58 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 60 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 63 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 65 | 0.75 | 0.16 | 0.12 | 3 | 0.36
|  |  |  | 57 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 59 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 61 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 62 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 64 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | 66 | 0.8 | 0.16 | 0.128 | 3 | 0.384
|  |  |  | 67 | 0.6 | 0.16 | 0.096 | 3 | 0.288
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | x former |  |  | 0.025 | 10 | 0.25
|  |  |  | Calculation |  |  | 1.551 |  | 5.878 | 3.7898 | 0.415 | 2.4394 | 15.51 | 58.78
[11 empty] | Total | 13.9689 | 2000.79 | 4693.77
|  | 1290 | total customers
|  | 11300400 | total (customers*8760)
|  | 2000.79 | total F
|  | 1.551 | SAIFI=total F/total customers
|  | 3.6386 | SAIDI=total G/total customers
|  | 2.346 | CAIDI=SAIDI/SAIFI
|  | 0.99958 | ASAI=total(customers*8760)-total G/total (customers*8760)
|  | 0.00041536 | ASUI=1-ASAI
|  | 13968.8725 | ENS=total ENS*1000
|  | 10.8286 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 3124.62 | 1100 | 20884.5 | 1100 | 8319.42 | 1100 | 5630.6625 | 1100 | 3124.62 | 1100 | 13689.2625 | 1100
Feeder 2 | 1828 | 3 | 7308 | 3 | 4908 | 3 | 2228 | 3 | 1828 | 3 | 5288 | 3
Feeder 3 | 3044.91 | 1080 | 20284.11 | 1080 | 8558.13 | 1080 | 5441.8975 | 1080 | 3044.91 | 1080 | 13505.035 | 1080
Feeder 4 | 3560.02 | 1300 | 26016.88 | 1300 | 9655.22 | 1300 | 6971.643 | 1300 | 3560.02 | 1300 | 16817.58 | 1300
Feeder 5 | 1548 | 3 | 6192 | 3 | 4128 | 3 | 1892 | 3 | 1548 | 3 | 4552 | 3
Feeder 6 | 1738 | 3 | 7224 | 3 | 5028 | 3 | 2104 | 3 | 1738 | 3 | 5484 | 3
Feeder 7 | 3174.43 | 1290 | 21131.41 | 1290 | 9003.55 | 1290 | 5709.523 | 1290 | 3174.43 | 1290 | 13968.87 | 1290
TOTAL | 18017.98 | 4779 | 109040.9 | 4779 | 49600.32 | 4779 | 29977.726 | 4779 | 18017.98 | 4779 | 73304.7475 | 4779
Analytic | 18.018 |  | 109.0409 |  | 49.6003 |  | 29.9777 |  | 18.018 |  | 73.3047
Monte Carlo_Code | 18.015 |  | 109.04 |  | 48.359 |  | 29.976 |  | 18.017 |  | 73.077
Deviation | 0.016539 |  | 0.00082538 |  | 2.5026 |  | 0.0057576 |  | 0.005439 |  | 0.31069
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 18.015 | 18.011 | 18.007 | 18.027 |  | 945000 | 109 | 109.04 | 109.01 | 109.08
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 48.298 | 48.335 | 48.359 | 48.348 |  | 47500 | 29.957 | 30.025 | 29.976 | 29.959
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 18.017 | 18.032 | 18.027 | 18.014 |  | 1140000 | 73.003 | 73.035 | 73.069 | 73.077