## F1_(1-7)
CASE A
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.025 | 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
0.025 |  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
0.025 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | Calculation |  |  | 0.2075 |  | 1.0913 | 5.259 | 0.545 | 0.59473 | 45.65 | 240.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21125 |  | 1.1025 | 5.2189 | 0.545 | 0.60086 | 46.475 | 242.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.0913 | 5.259 | 0.545 | 0.59473 | 45.65 | 240.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1062 | 4.7838 | 0.545 | 0.60291 | 50.875 | 243.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1025 | 4.7676 | 0.5 | 0.55125 | 46.25 | 220.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1062 | 4.7838 | 0.415 | 0.45909 | 2.3125 | 11.0625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1025 | 4.7676 | 0.415 | 0.45754 | 2.3125 | 11.025
[10 empty] | Total | 3.8611 | 239.525 | 1208.6625
| 1100 | total customers
| 9636000 | total (customers*8760)
| 239.525 | total F
| 0.21775 | SAIFI=total F/total customers
| 1.0988 | SAIDI=total G/total customers
| 5.0461 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012543 | ASUI=1-ASAI
| 3861.1125 | ENS=total ENS*1000
| 3.5101 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.545 | 4.1727 | 202.125 | 1684.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.545 | 4.1727 | 202.125 | 1684.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.545 | 4.1727 | 202.125 | 1684.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.545 | 4.1727 | 202.125 | 1684.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.5 | 3.8281 | 183.75 | 1531.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.415 | 3.1773 | 9.1875 | 76.5625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.415 | 3.1773 | 9.1875 | 76.5625
[10 empty] | Total | 26.8734 | 1010.625 | 8421.875
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1010.625 | total F
| 0.91875 | SAIFI=total F/total customers
| 7.6562 | SAIDI=total G/total customers
| 8.3333 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.000874 | ASUI=1-ASAI
| 26873.4375 | ENS=total ENS*1000
| 24.4304 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.3225 | 6.3735 | 0.545 | 0.72076 | 45.65 | 290.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21125 |  | 1.3337 | 6.3136 | 0.545 | 0.72689 | 46.475 | 293.425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.3225 | 6.3735 | 0.545 | 0.72076 | 45.65 | 290.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.3375 | 5.7838 | 0.545 | 0.72894 | 50.875 | 294.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.3337 | 5.7676 | 0.5 | 0.66687 | 46.25 | 266.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.3375 | 5.7838 | 0.415 | 0.55506 | 2.3125 | 13.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.3337 | 5.7676 | 0.415 | 0.55351 | 2.3125 | 13.3375
[10 empty] | Total | 4.6728 | 239.525 | 1463.0375
| 1100 | total customers
| 9636000 | total (customers*8760)
| 239.525 | total F
| 0.21775 | SAIFI=total F/total customers
| 1.33 | SAIDI=total G/total customers
| 6.1081 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015183 | ASUI=1-ASAI
| 4672.8 | ENS=total ENS*1000
| 4.248 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 1.4469 | 1.5748 | 0.545 | 0.78855 | 202.125 | 318.3125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 1.4563 | 1.585 | 0.545 | 0.79366 | 202.125 | 320.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 1.4469 | 1.5748 | 0.545 | 0.78855 | 202.125 | 318.3125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 2.4562 | 2.6735 | 0.545 | 1.3387 | 202.125 | 540.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 2.4562 | 2.6735 | 0.5 | 1.2281 | 183.75 | 491.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 2.4562 | 2.6735 | 0.415 | 1.0193 | 9.1875 | 24.5625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 2.4562 | 2.6735 | 0.415 | 1.0193 | 9.1875 | 24.5625
[10 empty] | Total | 6.9762 | 1010.625 | 2037.75
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1010.625 | total F
| 0.91875 | SAIFI=total F/total customers
| 1.8525 | SAIDI=total G/total customers
| 2.0163 | CAIDI=SAIDI/SAIFI
| 0.99979 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00021147 | ASUI=1-ASAI
| 6976.2187 | ENS=total ENS*1000
| 6.342 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.0913 | 5.259 | 0.545 | 0.59473 | 45.65 | 240.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21125 |  | 1.1025 | 5.2189 | 0.545 | 0.60086 | 46.475 | 242.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.0913 | 5.259 | 0.545 | 0.59473 | 45.65 | 240.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1062 | 4.7838 | 0.545 | 0.60291 | 50.875 | 243.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1025 | 4.7676 | 0.5 | 0.55125 | 46.25 | 220.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1062 | 4.7838 | 0.415 | 0.45909 | 2.3125 | 11.0625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.23125 |  | 1.1025 | 4.7676 | 0.415 | 0.45754 | 2.3125 | 11.025
[10 empty] | Total | 3.8611 | 239.525 | 1208.6625
| 1100 | total customers
| 9636000 | total (customers*8760)
| 239.525 | total F
| 0.21775 | SAIFI=total F/total customers
| 1.0988 | SAIDI=total G/total customers
| 5.0461 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012543 | ASUI=1-ASAI
| 3861.1125 | ENS=total ENS*1000
| 3.5101 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 1.4938 | 1.6259 | 0.545 | 0.81409 | 202.125 | 328.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 2.5406 | 2.7653 | 0.545 | 1.3846 | 202.125 | 558.9375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 3.5781 | 3.8946 | 0.545 | 1.9501 | 202.125 | 787.1875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 5.6219 | 6.119 | 0.545 | 3.0639 | 202.125 | 1236.8125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91875 |  | 5.6219 | 6.119 | 0.5 | 2.8109 | 183.75 | 1124.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.415 | 3.1773 | 9.1875 | 76.5625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 3 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 5 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 7 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 10 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 2 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 4 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 6 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 8 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 9 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 11 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 12 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91875 |  | 7.6562 | 8.3333 | 0.415 | 3.1773 | 9.1875 | 76.5625
[10 empty] | Total | 16.3784 | 1010.625 | 4189.0625
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1010.625 | total F
| 0.91875 | SAIFI=total F/total customers
| 3.8082 | SAIDI=total G/total customers
| 4.145 | CAIDI=SAIDI/SAIFI
| 0.99957 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00043473 | ASUI=1-ASAI
| 16378.3594 | ENS=total ENS*1000
| 14.8894 | AENS=ENS/total customers

## F2_(8-10)
CASE A & E
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.025 | 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
0.025 |  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
0.025 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | Calculation |  |  | 0.07 |  | 0.0725 | 1.0357 | 1 | 0.0725 | 0.07 | 0.0725
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.08375 | 1.1356 | 1.5 | 0.12563 | 0.07375 | 0.08375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.075 |  | 0.0875 | 1.1667 | 1 | 0.0875 | 0.075 | 0.0875
[10 empty] | Total | 0.28563 | 0.21875 | 0.24375
| 3 | total customers
| 26280 | total (customers*8760)
| 0.21875 | total F
| 0.072917 | SAIFI=total F/total customers
| 0.08125 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 9.2751e-06 | ASUI=1-ASAI
| 285.625 | ENS=total ENS*1000
| 95.2083 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.32625 | 3 | 1 | 0.32625 | 0.10875 | 0.32625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.32625 | 3 | 1.5 | 0.48938 | 0.10875 | 0.32625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.32625 | 3 | 1 | 0.32625 | 0.10875 | 0.32625
[10 empty] | Total | 1.1419 | 0.32625 | 0.97875
| 3 | total customers
| 26280 | total (customers*8760)
| 0.32625 | total F
| 0.10875 | SAIFI=total F/total customers
| 0.32625 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.7243e-05 | ASUI=1-ASAI
| 1141.875 | ENS=total ENS*1000
| 380.625 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07 |  | 0.21 | 3 | 1 | 0.21 | 0.07 | 0.21
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.22125 | 3 | 1.5 | 0.33188 | 0.07375 | 0.22125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.075 |  | 0.225 | 3 | 1 | 0.225 | 0.075 | 0.225
[10 empty] | Total | 0.76688 | 0.21875 | 0.65625
| 3 | total customers
| 26280 | total (customers*8760)
| 0.21875 | total F
| 0.072917 | SAIFI=total F/total customers
| 0.21875 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.4971e-05 | ASUI=1-ASAI
| 766.875 | ENS=total ENS*1000
| 255.625 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 18 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | Calculation |  |  | 0.10875 |  | 0.091875 | 0.84483 | 1 | 0.091875 | 0.10875 | 0.091875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | Calculation |  |  | 0.10875 |  | 0.10125 | 0.93103 | 1.5 | 0.15188 | 0.10875 | 0.10125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.10438 | 0.95977 | 1 | 0.10438 | 0.10875 | 0.10438
[10 empty] | Total | 0.34813 | 0.32625 | 0.2975
| 3 | total customers
| 26280 | total (customers*8760)
| 0.32625 | total F
| 0.10875 | SAIFI=total F/total customers
| 0.099167 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.132e-05 | ASUI=1-ASAI
| 348.125 | ENS=total ENS*1000
| 116.0417 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 18 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | Calculation |  |  | 0.10875 |  | 0.14188 | 1.3046 | 1 | 0.14188 | 0.10875 | 0.14188
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | Calculation |  |  | 0.10875 |  | 0.23875 | 2.1954 | 1.5 | 0.35813 | 0.10875 | 0.23875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 15 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 17 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 14 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 16 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 18 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | Calculation |  |  | 0.10875 |  | 0.32625 | 3 | 1 | 0.32625 | 0.10875 | 0.32625
[10 empty] | Total | 0.82625 | 0.32625 | 0.70688
| 3 | total customers
| 26280 | total (customers*8760)
| 0.32625 | total F
| 0.10875 | SAIFI=total F/total customers
| 0.23563 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.6898e-05 | ASUI=1-ASAI
| 826.25 | ENS=total ENS*1000
| 275.4167 | AENS=ENS/total customers

## F3_(11-17)
CASE A
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.025 | 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
0.025 |  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
0.025 |  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
0.025 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | Calculation |  |  | 0.20875 |  | 1.1044 | 5.2904 | 0.545 | 0.60188 | 45.925 | 242.9625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.1006 | 5.3042 | 0.545 | 0.59984 | 45.65 | 242.1375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.1006 | 5.3042 | 0.545 | 0.59984 | 45.65 | 242.1375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.0894 | 4.8961 | 0.5 | 0.54469 | 44.5 | 217.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.1006 | 4.9466 | 0.5 | 0.55031 | 44.5 | 220.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.1006 | 4.9466 | 0.415 | 0.45676 | 2.225 | 11.0062
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.0894 | 4.8961 | 0.415 | 0.45209 | 2.225 | 10.8938
[10 empty] | Total | 3.8054 | 230.675 | 1187.1375
| 1080 | total customers
| 9460800 | total (customers*8760)
| 230.675 | total F
| 0.21359 | SAIFI=total F/total customers
| 1.0992 | SAIDI=total G/total customers
| 5.1464 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012548 | ASUI=1-ASAI
| 3805.4156 | ENS=total ENS*1000
| 3.5235 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.545 | 4.1645 | 201.025 | 1681.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.545 | 4.1645 | 201.025 | 1681.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.545 | 4.1645 | 201.025 | 1681.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.5 | 3.8206 | 182.75 | 1528.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.5 | 3.8206 | 182.75 | 1528.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.415 | 3.1711 | 9.1375 | 76.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.415 | 3.1711 | 9.1375 | 76.4125
[10 empty] | Total | 26.4769 | 986.85 | 8252.55
| 1080 | total customers
| 9460800 | total (customers*8760)
| 986.85 | total F
| 0.91375 | SAIFI=total F/total customers
| 7.6413 | SAIDI=total G/total customers
| 8.3625 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00087229 | ASUI=1-ASAI
| 26476.9313 | ENS=total ENS*1000
| 24.5157 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.20875 |  | 1.3262 | 6.3533 | 0.545 | 0.72281 | 45.925 | 291.775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.3225 | 6.3735 | 0.545 | 0.72076 | 45.65 | 290.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.3225 | 6.3735 | 0.545 | 0.72076 | 45.65 | 290.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.3675 | 6.1461 | 0.5 | 0.68375 | 44.5 | 273.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.3675 | 6.1461 | 0.5 | 0.68375 | 44.5 | 273.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.3675 | 6.1461 | 0.415 | 0.56751 | 2.225 | 13.675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.3675 | 6.1461 | 0.415 | 0.56751 | 2.225 | 13.675
[10 empty] | Total | 4.6669 | 230.675 | 1448.025
| 1080 | total customers
| 9460800 | total (customers*8760)
| 230.675 | total F
| 0.21359 | SAIFI=total F/total customers
| 1.3408 | SAIDI=total G/total customers
| 6.2773 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015306 | ASUI=1-ASAI
| 4666.8563 | ENS=total ENS*1000
| 4.3212 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 1.4569 | 1.5944 | 0.545 | 0.794 | 201.025 | 320.5125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 1.4538 | 1.591 | 0.545 | 0.79229 | 201.025 | 319.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 2.4412 | 2.6717 | 0.545 | 1.3305 | 201.025 | 537.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 2.4412 | 2.6717 | 0.5 | 1.2206 | 182.75 | 488.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 1.4538 | 1.591 | 0.5 | 0.72688 | 182.75 | 290.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 2.4412 | 2.6717 | 0.415 | 1.0131 | 9.1375 | 24.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 2.4412 | 2.6717 | 0.415 | 1.0131 | 9.1375 | 24.4125
[10 empty] | Total | 6.8905 | 986.85 | 2005.2375
| 1080 | total customers
| 9460800 | total (customers*8760)
| 986.85 | total F
| 0.91375 | SAIFI=total F/total customers
| 1.8567 | SAIDI=total G/total customers
| 2.032 | CAIDI=SAIDI/SAIFI
| 0.99979 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00021195 | ASUI=1-ASAI
| 6890.5094 | ENS=total ENS*1000
| 6.3801 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.20875 |  | 1.1044 | 5.2904 | 0.545 | 0.60188 | 45.925 | 242.9625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.1006 | 5.3042 | 0.545 | 0.59984 | 45.65 | 242.1375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2075 |  | 1.1006 | 5.3042 | 0.545 | 0.59984 | 45.65 | 242.1375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.0894 | 4.8961 | 0.5 | 0.54469 | 44.5 | 217.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.1006 | 4.9466 | 0.5 | 0.55031 | 44.5 | 220.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.1006 | 4.9466 | 0.415 | 0.45676 | 2.225 | 11.0062
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0 | 0
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.2225 |  | 1.0894 | 4.8961 | 0.415 | 0.45209 | 2.225 | 10.8938
[10 empty] | Total | 3.8054 | 230.675 | 1187.1375
| 1080 | total customers
| 9460800 | total (customers*8760)
| 230.675 | total F
| 0.21359 | SAIFI=total F/total customers
| 1.0992 | SAIDI=total G/total customers
| 5.1464 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012548 | ASUI=1-ASAI
| 3805.4156 | ENS=total ENS*1000
| 3.5235 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 1.5038 | 1.6457 | 0.545 | 0.81954 | 201.025 | 330.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 25 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 2.5381 | 2.7777 | 0.545 | 1.3833 | 201.025 | 558.3875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 4.5725 | 5.0041 | 0.545 | 2.492 | 201.025 | 1005.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.91375 |  | 4.5725 | 5.0041 | 0.5 | 2.2862 | 182.75 | 914.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 30 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.5194 | 8.2291 | 0.5 | 3.7597 | 182.75 | 1503.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.415 | 3.1711 | 9.1375 | 76.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 21 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 23 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 26 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 28 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 20 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 22 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 24 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 25 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 27 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 29 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 30 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.91375 |  | 7.6413 | 8.3625 | 0.415 | 3.1711 | 9.1375 | 76.4125
[10 empty] | Total | 17.083 | 986.85 | 4466.3625
| 1080 | total customers
| 9460800 | total (customers*8760)
| 986.85 | total F
| 0.91375 | SAIFI=total F/total customers
| 4.1355 | SAIDI=total G/total customers
| 4.5259 | CAIDI=SAIDI/SAIFI
| 0.99953 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00047209 | ASUI=1-ASAI
| 17083.0094 | ENS=total ENS*1000
| 15.8176 | AENS=ENS/total customers

## F4_(18-25)
CASE A
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.025 | 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
0.025 |  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
0.025 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.545 | 0.59541 | 46.2 | 240.35
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.5 | 0.54625 | 42 | 218.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.5 | 0.55188 | 42.75 | 220.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.415 | 0.45806 | 2.1375 | 11.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.415 | 0.45339 | 2.1 | 10.925
[10 empty] | Total | 4.4096 | 276.2625 | 1430.0375
| 1300 | total customers
| 11388000 | total (customers*8760)
| 276.2625 | total F
| 0.21251 | SAIFI=total F/total customers
| 1.1 | SAIDI=total G/total customers
| 5.1764 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012557 | ASUI=1-ASAI
| 4409.6125 | ENS=total ENS*1000
| 3.392 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.545 | 4.7422 | 227.425 | 1914.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.545 | 4.7422 | 227.425 | 1914.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.545 | 4.7422 | 227.425 | 1914.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.545 | 4.7422 | 227.425 | 1914.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.5 | 4.3506 | 206.75 | 1740.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.5 | 4.3506 | 206.75 | 1740.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.415 | 3.611 | 10.3375 | 87.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.415 | 3.611 | 10.3375 | 87.0125
[10 empty] | Total | 34.892 | 1343.875 | 11311.625
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1343.875 | total F
| 1.0337 | SAIFI=total F/total customers
| 8.7013 | SAIDI=total G/total customers
| 8.4172 | CAIDI=SAIDI/SAIFI
| 0.99901 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00099329 | ASUI=1-ASAI
| 34892.0125 | ENS=total ENS*1000
| 26.84 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.545 | 0.73098 | 47.025 | 295.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.545 | 0.72485 | 46.2 | 292.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.545 | 0.73098 | 47.025 | 295.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.545 | 0.73098 | 47.025 | 295.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.5 | 0.665 | 42 | 266
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.5 | 0.67063 | 42.75 | 268.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.3413 | 6.2749 | 0.415 | 0.55662 | 2.1375 | 13.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.415 | 0.55195 | 2.1 | 13.3
[10 empty] | Total | 5.362 | 276.2625 | 1738.7875
| 1300 | total customers
| 11388000 | total (customers*8760)
| 276.2625 | total F
| 0.21251 | SAIFI=total F/total customers
| 1.3375 | SAIDI=total G/total customers
| 6.294 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015269 | ASUI=1-ASAI
| 5361.9875 | ENS=total ENS*1000
| 4.1246 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 1.5138 | 1.4643 | 0.545 | 0.82499 | 227.425 | 333.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.545 | 1.3632 | 227.425 | 550.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.545 | 1.3632 | 227.425 | 550.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.545 | 1.3632 | 227.425 | 550.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.5 | 1.2506 | 206.75 | 500.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 1.5138 | 1.4643 | 0.5 | 0.75688 | 206.75 | 302.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.415 | 1.038 | 10.3375 | 25.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 2.5012 | 2.4196 | 0.415 | 1.038 | 10.3375 | 25.0125
[10 empty] | Total | 8.9981 | 1343.875 | 2836.875
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1343.875 | total F
| 1.0337 | SAIFI=total F/total customers
| 2.1822 | SAIDI=total G/total customers
| 2.111 | CAIDI=SAIDI/SAIFI
| 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00024911 | ASUI=1-ASAI
| 8998.075 | ENS=total ENS*1000
| 6.9216 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.545 | 0.59541 | 46.2 | 240.35
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.545 | 0.60154 | 47.025 | 242.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.5 | 0.54625 | 42 | 218.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.5 | 0.55188 | 42.75 | 220.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21375 |  | 1.1038 | 5.1637 | 0.415 | 0.45806 | 2.1375 | 11.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.0925 | 5.2024 | 0.415 | 0.45339 | 2.1 | 10.925
[10 empty] | Total | 4.4096 | 276.2625 | 1430.0375
| 1300 | total customers
| 11388000 | total (customers*8760)
| 276.2625 | total F
| 0.21251 | SAIFI=total F/total customers
| 1.1 | SAIDI=total G/total customers
| 5.1764 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012557 | ASUI=1-ASAI
| 4409.6125 | ENS=total ENS*1000
| 3.392 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 1.5638 | 1.5127 | 0.545 | 0.85224 | 227.425 | 344.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 3.5981 | 3.4807 | 0.545 | 1.961 | 227.425 | 791.5875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 38 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 3.5981 | 3.4807 | 0.545 | 1.961 | 227.425 | 791.5875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 5.6325 | 5.4486 | 0.545 | 3.0697 | 227.425 | 1239.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 5.6325 | 5.4486 | 0.5 | 2.8162 | 206.75 | 1126.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 43 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.0337 |  | 6.6794 | 6.4613 | 0.5 | 3.3397 | 206.75 | 1335.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.415 | 3.611 | 10.3375 | 87.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 33 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 36 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 39 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 41 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 32 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 34 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 35 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 37 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 38 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 40 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 42 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 43 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.0337 |  | 8.7012 | 8.4172 | 0.415 | 3.611 | 10.3375 | 87.0125
[10 empty] | Total | 21.2219 | 1343.875 | 5802.75
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1343.875 | total F
| 1.0337 | SAIFI=total F/total customers
| 4.4637 | SAIDI=total G/total customers
| 4.3179 | CAIDI=SAIDI/SAIFI
| 0.99949 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00050955 | ASUI=1-ASAI
| 21221.8875 | ENS=total ENS*1000
| 16.3245 | AENS=ENS/total customers

## F5_(26-28)
CASE A & E
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.025 | 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
0.025 |  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
0.025 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | Calculation |  |  | 0.0725 |  | 0.083125 | 1.1466 | 1 | 0.083125 | 0.0725 | 0.083125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.086875 | 1.178 | 1 | 0.086875 | 0.07375 | 0.086875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.06875 |  | 0.071875 | 1.0455 | 1 | 0.071875 | 0.06875 | 0.071875
[10 empty] | Total | 0.24188 | 0.215 | 0.24188
| 3 | total customers
| 26280 | total (customers*8760)
| 0.215 | total F
| 0.071667 | SAIFI=total F/total customers
| 0.080625 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 9.2038e-06 | ASUI=1-ASAI
| 241.875 | ENS=total ENS*1000
| 80.625 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
[10 empty] | Total | 0.9675 | 0.3225 | 0.9675
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.3225 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.6815e-05 | ASUI=1-ASAI
| 967.5 | ENS=total ENS*1000
| 322.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.0725 |  | 0.2175 | 3 | 1 | 0.2175 | 0.0725 | 0.2175
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.22125 | 3 | 1 | 0.22125 | 0.07375 | 0.22125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.06875 |  | 0.20625 | 3 | 1 | 0.20625 | 0.06875 | 0.20625
[10 empty] | Total | 0.645 | 0.215 | 0.645
| 3 | total customers
| 26280 | total (customers*8760)
| 0.215 | total F
| 0.071667 | SAIFI=total F/total customers
| 0.215 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.4543e-05 | ASUI=1-ASAI
| 645 | ENS=total ENS*1000
| 215 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 49 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.10063 | 0.93605 | 1 | 0.10063 | 0.1075 | 0.10063
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.10375 | 0.96512 | 1 | 0.10375 | 0.1075 | 0.10375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 47 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.09125 | 0.84884 | 1 | 0.09125 | 0.1075 | 0.09125
[10 empty] | Total | 0.29563 | 0.3225 | 0.29563
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.098542 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.1249e-05 | ASUI=1-ASAI
| 295.625 | ENS=total ENS*1000
| 98.5417 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 49 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.15063 | 1.4012 | 1 | 0.15063 | 0.1075 | 0.15063
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.23813 | 2.2151 | 1 | 0.23813 | 0.1075 | 0.23813
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 46 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 48 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 45 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 47 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 49 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
[10 empty] | Total | 0.71125 | 0.3225 | 0.71125
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.23708 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.7064e-05 | ASUI=1-ASAI
| 711.25 | ENS=total ENS*1000
| 237.0833 | AENS=ENS/total customers

## F6_(29-31)
CASE A & E
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.025 | 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
0.025 |  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
0.025 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
0.025 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | Calculation |  |  | 0.07375 |  | 0.074375 | 1.0085 | 1 | 0.074375 | 0.07375 | 0.074375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.0775 |  | 0.085625 | 1.1048 | 1 | 0.085625 | 0.0775 | 0.085625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.07375 |  | 0.074375 | 1.0085 | 1.5 | 0.11156 | 0.07375 | 0.074375
[10 empty] | Total | 0.27156 | 0.225 | 0.23438
| 3 | total customers
| 26280 | total (customers*8760)
| 0.225 | total F
| 0.075 | SAIFI=total F/total customers
| 0.078125 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 8.9184e-06 | ASUI=1-ASAI
| 271.5625 | ENS=total ENS*1000
| 90.5208 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1 | 0.3225 | 0.1075 | 0.3225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1.5 | 0.48375 | 0.1075 | 0.3225
[10 empty] | Total | 1.1288 | 0.3225 | 0.9675
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.3225 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.6815e-05 | ASUI=1-ASAI
| 1128.75 | ENS=total ENS*1000
| 376.25 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.07375 |  | 0.22125 | 3 | 1 | 0.22125 | 0.07375 | 0.22125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.0775 |  | 0.2325 | 3 | 1 | 0.2325 | 0.0775 | 0.2325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.07375 |  | 0.22125 | 3 | 1.5 | 0.33188 | 0.07375 | 0.22125
[10 empty] | Total | 0.78563 | 0.225 | 0.675
| 3 | total customers
| 26280 | total (customers*8760)
| 0.225 | total F
| 0.075 | SAIFI=total F/total customers
| 0.225 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.5685e-05 | ASUI=1-ASAI
| 785.625 | ENS=total ENS*1000
| 261.875 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 55 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.09125 | 0.84884 | 1 | 0.09125 | 0.1075 | 0.09125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.10063 | 0.93605 | 1 | 0.10063 | 0.1075 | 0.10063
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.09125 | 0.84884 | 1.5 | 0.13687 | 0.1075 | 0.09125
[10 empty] | Total | 0.32875 | 0.3225 | 0.28313
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.094375 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.0773e-05 | ASUI=1-ASAI
| 328.75 | ENS=total ENS*1000
| 109.5833 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 55 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.13813 | 1.2849 | 1 | 0.13813 | 0.1075 | 0.13813
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | Calculation |  |  | 0.1075 |  | 0.235 | 2.186 | 1 | 0.235 | 0.1075 | 0.235
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 52 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 54 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 51 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 53 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 55 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | Calculation |  |  | 0.1075 |  | 0.3225 | 3 | 1.5 | 0.48375 | 0.1075 | 0.3225
[10 empty] | Total | 0.85688 | 0.3225 | 0.69563
| 3 | total customers
| 26280 | total (customers*8760)
| 0.3225 | total F
| 0.1075 | SAIFI=total F/total customers
| 0.23188 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.647e-05 | ASUI=1-ASAI
| 856.875 | ENS=total ENS*1000
| 285.625 | AENS=ENS/total customers

## F7_(32-38)
CASE A
0.025 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.025 | 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
0.025 |  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
0.025 |  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
0.025 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.025 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.025 |  |  | x former |  |  | 0.1 | 10 | 1
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | x former |  |  | 0 | 0 | 0
0.025 |  |  | Calculation |  |  | 0.21 |  | 1.105 | 5.2619 | 0.545 | 0.60223 | 46.2 | 243.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.105 | 5.2619 | 0.545 | 0.60223 | 46.2 | 243.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.205 |  | 1.09 | 5.3171 | 0.545 | 0.59405 | 45.1 | 239.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.105 | 4.9111 | 0.545 | 0.60223 | 49.5 | 243.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.09 | 4.8444 | 0.5 | 0.545 | 45 | 218
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.105 | 4.9111 | 0.5 | 0.5525 | 45 | 221
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.09 | 4.8444 | 0.415 | 0.45235 | 2.25 | 10.9
[10 empty] | Total | 3.9506 | 279.25 | 1419
| 1290 | total customers
| 11300400 | total (customers*8760)
| 279.25 | total F
| 0.21647 | SAIFI=total F/total customers
| 1.1 | SAIDI=total G/total customers
| 5.0815 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012557 | ASUI=1-ASAI
| 3950.575 | ENS=total ENS*1000
| 3.0625 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.545 | 4.1665 | 201.3 | 1681.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.545 | 4.1665 | 201.3 | 1681.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.545 | 4.1665 | 201.3 | 1681.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.545 | 4.1665 | 201.3 | 1681.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.5 | 3.8225 | 183 | 1529
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.5 | 3.8225 | 183 | 1529
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.415 | 3.1727 | 9.15 | 76.45
[10 empty] | Total | 27.4838 | 1180.35 | 9862.05
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1180.35 | total F
| 0.915 | SAIFI=total F/total customers
| 7.645 | SAIDI=total G/total customers
| 8.3552 | CAIDI=SAIDI/SAIFI
| 0.99913 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00087272 | ASUI=1-ASAI
| 27483.775 | ENS=total ENS*1000
| 21.3053 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.545 | 0.72485 | 46.2 | 292.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.33 | 6.3333 | 0.545 | 0.72485 | 46.2 | 292.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.205 |  | 1.315 | 6.4146 | 0.545 | 0.71668 | 45.1 | 289.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.375 | 6.1111 | 0.545 | 0.74938 | 49.5 | 302.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.375 | 6.1111 | 0.5 | 0.6875 | 45 | 275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.375 | 6.1111 | 0.5 | 0.6875 | 45 | 275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.375 | 6.1111 | 0.415 | 0.57062 | 2.25 | 13.75
[10 empty] | Total | 4.8614 | 279.25 | 1740.75
| 1290 | total customers
| 11300400 | total (customers*8760)
| 279.25 | total F
| 0.21647 | SAIFI=total F/total customers
| 1.3494 | SAIDI=total G/total customers
| 6.2337 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015404 | ASUI=1-ASAI
| 4861.375 | ENS=total ENS*1000
| 3.7685 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 1.4575 | 1.5929 | 0.545 | 0.79434 | 201.3 | 320.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 1.4575 | 1.5929 | 0.545 | 0.79434 | 201.3 | 320.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 2.445 | 2.6721 | 0.545 | 1.3325 | 201.3 | 537.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 2.445 | 2.6721 | 0.545 | 1.3325 | 201.3 | 537.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 1.445 | 1.5792 | 0.5 | 0.7225 | 183 | 289
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 2.445 | 2.6721 | 0.5 | 1.2225 | 183 | 489
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 2.445 | 2.6721 | 0.415 | 1.0147 | 9.15 | 24.45
[10 empty] | Total | 7.2134 | 1180.35 | 2519.55
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1180.35 | total F
| 0.915 | SAIFI=total F/total customers
| 1.9531 | SAIDI=total G/total customers
| 2.1346 | CAIDI=SAIDI/SAIFI
| 0.99978 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022296 | ASUI=1-ASAI
| 7213.4 | ENS=total ENS*1000
| 5.5918 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.105 | 5.2619 | 0.545 | 0.60223 | 46.2 | 243.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.21 |  | 1.105 | 5.2619 | 0.545 | 0.60223 | 46.2 | 243.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.205 |  | 1.09 | 5.3171 | 0.545 | 0.59405 | 45.1 | 239.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.105 | 4.9111 | 0.545 | 0.60223 | 49.5 | 243.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.09 | 4.8444 | 0.5 | 0.545 | 45 | 218
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.105 | 4.9111 | 0.5 | 0.5525 | 45 | 221
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0 | 0
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.225 |  | 1.09 | 4.8444 | 0.415 | 0.45235 | 2.25 | 10.9
[10 empty] | Total | 3.9506 | 279.25 | 1419
| 1290 | total customers
| 11300400 | total (customers*8760)
| 279.25 | total F
| 0.21647 | SAIFI=total F/total customers
| 1.1 | SAIDI=total G/total customers
| 5.0815 | CAIDI=SAIDI/SAIFI
| 0.99987 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00012557 | ASUI=1-ASAI
| 3950.575 | ENS=total ENS*1000
| 3.0625 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 1.5044 | 1.6441 | 0.545 | 0.81988 | 201.3 | 330.9625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 62 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 2.5419 | 2.778 | 0.545 | 1.3853 | 201.3 | 559.2125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 4.5762 | 5.0014 | 0.545 | 2.4941 | 201.3 | 1006.775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 4.5762 | 5.0014 | 0.545 | 2.4941 | 201.3 | 1006.775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 0.5 | 0.009375
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 0.5 | 0.01
|  |  | 67 | 0.6 | 0.025 | 0.015 | 0.5 | 0.0075
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 0.915 |  | 5.6106 | 6.1318 | 0.5 | 2.8053 | 183 | 1122.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.5 | 3.8225 | 183 | 1529
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 58 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 60 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 63 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 65 | 0.75 | 0.025 | 0.01875 | 3 | 0.05625
|  |  | 57 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 59 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 61 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 62 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 64 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | 66 | 0.8 | 0.025 | 0.02 | 3 | 0.06
|  |  | 67 | 0.6 | 0.025 | 0.015 | 3 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 0.915 |  | 7.645 | 8.3552 | 0.415 | 3.1727 | 9.15 | 76.45
[10 empty] | Total | 16.9938 | 1180.35 | 5631.3
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1180.35 | total F
| 0.915 | SAIFI=total F/total customers
| 4.3653 | SAIDI=total G/total customers
| 4.7709 | CAIDI=SAIDI/SAIFI
| 0.9995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00049833 | ASUI=1-ASAI
| 16993.8062 | ENS=total ENS*1000
| 13.1735 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 3861.1125 | 1100 | 26873.4375 | 1100 | 4672.8 | 1100 | 6976.2188 | 1100 | 3861.1125 | 1100 | 16378.3594 | 1100
Feeder 2 | 285.625 | 3 | 1141.875 | 3 | 766.875 | 3 | 348.125 | 3 | 285.625 | 3 | 826.25 | 3
Feeder 3 | 3805.4156 | 1080 | 26476.9313 | 1080 | 4666.8562 | 1080 | 6890.5094 | 1080 | 3805.4156 | 1080 | 17083.0094 | 1080
Feeder 4 | 4409.6125 | 1300 | 34892.0125 | 1300 | 5361.9875 | 1300 | 8998.075 | 1300 | 4409.6125 | 1300 | 21221.8875 | 1300
Feeder 5 | 241.875 | 3 | 967.5 | 3 | 645 | 3 | 295.625 | 3 | 241.875 | 3 | 711.25 | 3
Feeder 6 | 271.5625 | 3 | 1128.75 | 3 | 785.625 | 3 | 328.75 | 3 | 271.5625 | 3 | 856.875 | 3
Feeder 7 | 3950.575 | 1290 | 27483.775 | 1290 | 4861.375 | 1290 | 7213.4 | 1290 | 3950.575 | 1290 | 16993.8063 | 1290
TOTAL | 16825.7781 | 4779 | 118964.2812 | 4779 | 21760.5187 | 4779 | 31050.7031 | 4779 | 16825.7781 | 4779 | 74071.4375 | 4779
Analytic | 16.8258 |  | 118.9643 |  | 21.7605 |  | 31.0507 |  | 16.8258 |  | 74.0714
Monte Carlo_Code | 16.822 |  | 118.96 |  | 21.569 |  | 31.04 |  | 16.82 |  | 73.225
Deviation | 0.022454 |  | 0.0035988 |  | 0.88012 |  | 0.03447 |  | 0.034341 |  | 1.1427
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 16.798 | 16.826 | 16.828 | 16.822 |  | 945000 | 118.89 | 118.93 | 118.96 | 118.99
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 21.519 | 21.569 | 21.566 | 21.563 |  | 47500 | 31.062 | 31.018 | 31.04 | 31.023
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 16.818 | 16.82 | 16.848 | 16.852 |  | 1140000 | 73.113 | 73.163 | 73.147 | 73.225