## F1_(1-7)
CASE A
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.05 | 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
0.05 |  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
0.05 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | Calculation |  |  | 0.315 |  | 1.1825 | 3.754 | 0.545 | 0.64446 | 69.3 | 260.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3225 |  | 1.205 | 3.7364 | 0.545 | 0.65673 | 70.95 | 265.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.1825 | 3.754 | 0.545 | 0.64446 | 69.3 | 260.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.2125 | 3.3448 | 0.545 | 0.66081 | 79.75 | 266.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.205 | 3.3241 | 0.5 | 0.6025 | 72.5 | 241
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.2125 | 3.3448 | 0.415 | 0.50319 | 3.625 | 12.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.205 | 3.3241 | 0.415 | 0.50008 | 3.625 | 12.05
[10 empty] | Total | 4.2122 | 369.05 | 1317.325
| 1100 | total customers
| 9636000 | total (customers*8760)
| 369.05 | total F
| 0.3355 | SAIFI=total F/total customers
| 1.1976 | SAIDI=total G/total customers
| 3.5695 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013671 | ASUI=1-ASAI
| 4212.225 | ENS=total ENS*1000
| 3.8293 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.545 | 4.5303 | 250.25 | 1828.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.545 | 4.5303 | 250.25 | 1828.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.545 | 4.5303 | 250.25 | 1828.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.545 | 4.5303 | 250.25 | 1828.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.5 | 4.1562 | 227.5 | 1662.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.415 | 3.4497 | 11.375 | 83.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.415 | 3.4497 | 11.375 | 83.125
[10 empty] | Total | 29.1769 | 1251.25 | 9143.75
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1251.25 | total F
| 1.1375 | SAIFI=total F/total customers
| 8.3125 | SAIDI=total G/total customers
| 7.3077 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094892 | ASUI=1-ASAI
| 29176.875 | ENS=total ENS*1000
| 26.5244 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.645 | 5.2222 | 0.545 | 0.89653 | 69.3 | 361.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3225 |  | 1.6675 | 5.1705 | 0.545 | 0.90879 | 70.95 | 366.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.645 | 5.2222 | 0.545 | 0.89653 | 69.3 | 361.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.675 | 4.6207 | 0.545 | 0.91288 | 79.75 | 368.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.6675 | 4.6 | 0.5 | 0.83375 | 72.5 | 333.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.675 | 4.6207 | 0.415 | 0.69512 | 3.625 | 16.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.6675 | 4.6 | 0.415 | 0.69201 | 3.625 | 16.675
[10 empty] | Total | 5.8356 | 369.05 | 1826.075
| 1100 | total customers
| 9636000 | total (customers*8760)
| 369.05 | total F
| 0.3355 | SAIFI=total F/total customers
| 1.6601 | SAIDI=total G/total customers
| 4.948 | CAIDI=SAIDI/SAIFI
| 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018951 | ASUI=1-ASAI
| 5835.6 | ENS=total ENS*1000
| 5.3051 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 1.5938 | 1.4011 | 0.545 | 0.86859 | 250.25 | 350.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 1.6125 | 1.4176 | 0.545 | 0.87881 | 250.25 | 354.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 1.5938 | 1.4011 | 0.545 | 0.86859 | 250.25 | 350.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 2.6625 | 2.3407 | 0.545 | 1.4511 | 250.25 | 585.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 2.6625 | 2.3407 | 0.5 | 1.3312 | 227.5 | 532.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 2.6625 | 2.3407 | 0.415 | 1.1049 | 11.375 | 26.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 2.6625 | 2.3407 | 0.415 | 1.1049 | 11.375 | 26.625
[10 empty] | Total | 7.6082 | 1251.25 | 2227.5
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1251.25 | total F
| 1.1375 | SAIFI=total F/total customers
| 2.025 | SAIDI=total G/total customers
| 1.7802 | CAIDI=SAIDI/SAIFI
| 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023116 | ASUI=1-ASAI
| 7608.1875 | ENS=total ENS*1000
| 6.9165 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.1825 | 3.754 | 0.545 | 0.64446 | 69.3 | 260.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3225 |  | 1.205 | 3.7364 | 0.545 | 0.65673 | 70.95 | 265.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.1825 | 3.754 | 0.545 | 0.64446 | 69.3 | 260.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.2125 | 3.3448 | 0.545 | 0.66081 | 79.75 | 266.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.205 | 3.3241 | 0.5 | 0.6025 | 72.5 | 241
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.2125 | 3.3448 | 0.415 | 0.50319 | 3.625 | 12.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3625 |  | 1.205 | 3.3241 | 0.415 | 0.50008 | 3.625 | 12.05
[10 empty] | Total | 4.2122 | 369.05 | 1317.325
| 1100 | total customers
| 9636000 | total (customers*8760)
| 369.05 | total F
| 0.3355 | SAIFI=total F/total customers
| 1.1976 | SAIDI=total G/total customers
| 3.5695 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013671 | ASUI=1-ASAI
| 4212.225 | ENS=total ENS*1000
| 3.8293 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 1.6875 | 1.4835 | 0.545 | 0.91969 | 250.25 | 371.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 2.8312 | 2.489 | 0.545 | 1.543 | 250.25 | 622.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 3.9562 | 3.478 | 0.545 | 2.1562 | 250.25 | 870.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 6.1437 | 5.4011 | 0.545 | 3.3483 | 250.25 | 1351.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1375 |  | 6.1437 | 5.4011 | 0.5 | 3.0719 | 227.5 | 1228.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.415 | 3.4497 | 11.375 | 83.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 3 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 5 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 7 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 10 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 2 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 4 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 6 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 8 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 9 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 11 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 12 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1375 |  | 8.3125 | 7.3077 | 0.415 | 3.4497 | 11.375 | 83.125
[10 empty] | Total | 17.9385 | 1251.25 | 4611.125
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1251.25 | total F
| 1.1375 | SAIFI=total F/total customers
| 4.1919 | SAIDI=total G/total customers
| 3.6852 | CAIDI=SAIDI/SAIFI
| 0.99952 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00047853 | ASUI=1-ASAI
| 17938.4688 | ENS=total ENS*1000
| 16.3077 | AENS=ENS/total customers

## F2_(8-10)
CASE A & E
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.05 | 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
0.05 |  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
0.05 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | Calculation |  |  | 0.14 |  | 0.145 | 1.0357 | 1 | 0.145 | 0.14 | 0.145
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.1675 | 1.1356 | 1.5 | 0.25125 | 0.1475 | 0.1675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.15 |  | 0.175 | 1.1667 | 1 | 0.175 | 0.15 | 0.175
[10 empty] | Total | 0.57125 | 0.4375 | 0.4875
| 3 | total customers
| 26280 | total (customers*8760)
| 0.4375 | total F
| 0.14583 | SAIFI=total F/total customers
| 0.1625 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.855e-05 | ASUI=1-ASAI
| 571.25 | ENS=total ENS*1000
| 190.4167 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1 | 0.6525 | 0.2175 | 0.6525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1.5 | 0.97875 | 0.2175 | 0.6525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1 | 0.6525 | 0.2175 | 0.6525
[10 empty] | Total | 2.2838 | 0.6525 | 1.9575
| 3 | total customers
| 26280 | total (customers*8760)
| 0.6525 | total F
| 0.2175 | SAIFI=total F/total customers
| 0.6525 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.4486e-05 | ASUI=1-ASAI
| 2283.75 | ENS=total ENS*1000
| 761.25 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.14 |  | 0.42 | 3 | 1 | 0.42 | 0.14 | 0.42
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.4425 | 3 | 1.5 | 0.66375 | 0.1475 | 0.4425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.15 |  | 0.45 | 3 | 1 | 0.45 | 0.15 | 0.45
[10 empty] | Total | 1.5338 | 0.4375 | 1.3125
| 3 | total customers
| 26280 | total (customers*8760)
| 0.4375 | total F
| 0.14583 | SAIFI=total F/total customers
| 0.4375 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.9943e-05 | ASUI=1-ASAI
| 1533.75 | ENS=total ENS*1000
| 511.25 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 18 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | Calculation |  |  | 0.2175 |  | 0.18375 | 0.84483 | 1 | 0.18375 | 0.2175 | 0.18375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | Calculation |  |  | 0.2175 |  | 0.2025 | 0.93103 | 1.5 | 0.30375 | 0.2175 | 0.2025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.20875 | 0.95977 | 1 | 0.20875 | 0.2175 | 0.20875
[10 empty] | Total | 0.69625 | 0.6525 | 0.595
| 3 | total customers
| 26280 | total (customers*8760)
| 0.6525 | total F
| 0.2175 | SAIFI=total F/total customers
| 0.19833 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.2641e-05 | ASUI=1-ASAI
| 696.25 | ENS=total ENS*1000
| 232.0833 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 18 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | Calculation |  |  | 0.2175 |  | 0.28375 | 1.3046 | 1 | 0.28375 | 0.2175 | 0.28375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | Calculation |  |  | 0.2175 |  | 0.4775 | 2.1954 | 1.5 | 0.71625 | 0.2175 | 0.4775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 15 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 17 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 14 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 16 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 18 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1 | 0.6525 | 0.2175 | 0.6525
[10 empty] | Total | 1.6525 | 0.6525 | 1.4138
| 3 | total customers
| 26280 | total (customers*8760)
| 0.6525 | total F
| 0.2175 | SAIFI=total F/total customers
| 0.47125 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.3796e-05 | ASUI=1-ASAI
| 1652.5 | ENS=total ENS*1000
| 550.8333 | AENS=ENS/total customers

## F3_(11-17)
CASE A
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.05 | 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
0.05 |  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
0.05 |  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
0.05 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | Calculation |  |  | 0.3175 |  | 1.2087 | 3.8071 | 0.545 | 0.65877 | 69.85 | 265.925
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.2012 | 3.8135 | 0.545 | 0.65468 | 69.3 | 264.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.2012 | 3.8135 | 0.545 | 0.65468 | 69.3 | 264.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.1787 | 3.4167 | 0.5 | 0.58937 | 69 | 235.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.2012 | 3.4819 | 0.5 | 0.60062 | 69 | 240.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.2012 | 3.4819 | 0.415 | 0.49852 | 3.45 | 12.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.1787 | 3.4167 | 0.415 | 0.48918 | 3.45 | 11.7875
[10 empty] | Total | 4.1458 | 353.35 | 1294.275
| 1080 | total customers
| 9460800 | total (customers*8760)
| 353.35 | total F
| 0.32718 | SAIFI=total F/total customers
| 1.1984 | SAIDI=total G/total customers
| 3.6629 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001368 | ASUI=1-ASAI
| 4145.8312 | ENS=total ENS*1000
| 3.8387 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.545 | 4.514 | 248.05 | 1822.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.545 | 4.514 | 248.05 | 1822.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.545 | 4.514 | 248.05 | 1822.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.5 | 4.1413 | 225.5 | 1656.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.5 | 4.1413 | 225.5 | 1656.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.415 | 3.4372 | 11.275 | 82.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.415 | 3.4372 | 11.275 | 82.825
[10 empty] | Total | 28.6989 | 1217.7 | 8945.1
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1217.7 | total F
| 1.1275 | SAIFI=total F/total customers
| 8.2825 | SAIDI=total G/total customers
| 7.3459 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094549 | ASUI=1-ASAI
| 28698.8625 | ENS=total ENS*1000
| 26.573 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3175 |  | 1.6525 | 5.2047 | 0.545 | 0.90061 | 69.85 | 363.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.645 | 5.2222 | 0.545 | 0.89653 | 69.3 | 361.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.645 | 5.2222 | 0.545 | 0.89653 | 69.3 | 361.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.735 | 5.029 | 0.5 | 0.8675 | 69 | 347
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.735 | 5.029 | 0.5 | 0.8675 | 69 | 347
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.735 | 5.029 | 0.415 | 0.72002 | 3.45 | 17.35
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.735 | 5.029 | 0.415 | 0.72002 | 3.45 | 17.35
[10 empty] | Total | 5.8687 | 353.35 | 1816.05
| 1080 | total customers
| 9460800 | total (customers*8760)
| 353.35 | total F
| 0.32718 | SAIFI=total F/total customers
| 1.6815 | SAIDI=total G/total customers
| 5.1395 | CAIDI=SAIDI/SAIFI
| 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00019196 | ASUI=1-ASAI
| 5868.7125 | ENS=total ENS*1000
| 5.434 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 1.6138 | 1.4313 | 0.545 | 0.87949 | 248.05 | 355.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 1.6075 | 1.4257 | 0.545 | 0.87609 | 248.05 | 353.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 2.6325 | 2.3348 | 0.545 | 1.4347 | 248.05 | 579.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 2.6325 | 2.3348 | 0.5 | 1.3162 | 225.5 | 526.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 1.6075 | 1.4257 | 0.5 | 0.80375 | 225.5 | 321.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 2.6325 | 2.3348 | 0.415 | 1.0925 | 11.275 | 26.325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 2.6325 | 2.3348 | 0.415 | 1.0925 | 11.275 | 26.325
[10 empty] | Total | 7.4953 | 1217.7 | 2188.475
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1217.7 | total F
| 1.1275 | SAIFI=total F/total customers
| 2.0264 | SAIDI=total G/total customers
| 1.7972 | CAIDI=SAIDI/SAIFI
| 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023132 | ASUI=1-ASAI
| 7495.2688 | ENS=total ENS*1000
| 6.9401 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3175 |  | 1.2087 | 3.8071 | 0.545 | 0.65877 | 69.85 | 265.925
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.2012 | 3.8135 | 0.545 | 0.65468 | 69.3 | 264.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.315 |  | 1.2012 | 3.8135 | 0.545 | 0.65468 | 69.3 | 264.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.1787 | 3.4167 | 0.5 | 0.58937 | 69 | 235.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.2012 | 3.4819 | 0.5 | 0.60062 | 69 | 240.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.2012 | 3.4819 | 0.415 | 0.49852 | 3.45 | 12.0125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0 | 0
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.345 |  | 1.1787 | 3.4167 | 0.415 | 0.48918 | 3.45 | 11.7875
[10 empty] | Total | 4.1458 | 353.35 | 1294.275
| 1080 | total customers
| 9460800 | total (customers*8760)
| 353.35 | total F
| 0.32718 | SAIFI=total F/total customers
| 1.1984 | SAIDI=total G/total customers
| 3.6629 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001368 | ASUI=1-ASAI
| 4145.8312 | ENS=total ENS*1000
| 3.8387 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 1.7075 | 1.5144 | 0.545 | 0.93059 | 248.05 | 375.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 25 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 2.8262 | 2.5067 | 0.545 | 1.5403 | 248.05 | 621.775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 4.995 | 4.4302 | 0.545 | 2.7223 | 248.05 | 1098.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.1275 |  | 4.995 | 4.4302 | 0.5 | 2.4975 | 225.5 | 999
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 30 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.0388 | 7.1297 | 0.5 | 4.0194 | 225.5 | 1607.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.415 | 3.4372 | 11.275 | 82.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 21 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 23 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 26 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 28 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 20 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 22 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 24 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 25 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 27 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 29 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 30 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.1275 |  | 8.2825 | 7.3459 | 0.415 | 3.4372 | 11.275 | 82.825
[10 empty] | Total | 18.5845 | 1217.7 | 4868.725
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1217.7 | total F
| 1.1275 | SAIFI=total F/total customers
| 4.5081 | SAIDI=total G/total customers
| 3.9983 | CAIDI=SAIDI/SAIFI
| 0.99949 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00051462 | ASUI=1-ASAI
| 18584.5187 | ENS=total ENS*1000
| 17.2079 | AENS=ENS/total customers

## F4_(18-25)
CASE A
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.05 | 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
0.05 |  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
0.05 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.545 | 0.64583 | 70.4 | 260.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.5 | 0.5925 | 64 | 237
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.5 | 0.60375 | 65.5 | 241.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.415 | 0.50111 | 3.275 | 12.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.415 | 0.49178 | 3.2 | 11.85
[10 empty] | Total | 4.8092 | 422.525 | 1560.075
| 1300 | total customers
| 11388000 | total (customers*8760)
| 422.525 | total F
| 0.32502 | SAIFI=total F/total customers
| 1.2001 | SAIDI=total G/total customers
| 3.6923 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013699 | ASUI=1-ASAI
| 4809.225 | ENS=total ENS*1000
| 3.6994 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.545 | 5.1244 | 278.85 | 2068.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.545 | 5.1244 | 278.85 | 2068.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.545 | 5.1244 | 278.85 | 2068.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.545 | 5.1244 | 278.85 | 2068.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.5 | 4.7012 | 253.5 | 1880.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.5 | 4.7012 | 253.5 | 1880.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.415 | 3.902 | 12.675 | 94.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.415 | 3.902 | 12.675 | 94.025
[10 empty] | Total | 37.704 | 1647.75 | 12223.25
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1647.75 | total F
| 1.2675 | SAIFI=total F/total customers
| 9.4025 | SAIDI=total G/total customers
| 7.4181 | CAIDI=SAIDI/SAIFI
| 0.99893 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010733 | ASUI=1-ASAI
| 37704.025 | ENS=total ENS*1000
| 29.0031 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.545 | 0.91696 | 72.05 | 370.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.545 | 0.9047 | 70.4 | 365.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.545 | 0.91696 | 72.05 | 370.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.545 | 0.91696 | 72.05 | 370.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.5 | 0.83 | 64 | 332
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.5 | 0.84125 | 65.5 | 336.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.6825 | 5.1374 | 0.415 | 0.69824 | 3.275 | 16.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.415 | 0.6889 | 3.2 | 16.6
[10 empty] | Total | 6.714 | 422.525 | 2177.575
| 1300 | total customers
| 11388000 | total (customers*8760)
| 422.525 | total F
| 0.32502 | SAIFI=total F/total customers
| 1.6751 | SAIDI=total G/total customers
| 5.1537 | CAIDI=SAIDI/SAIFI
| 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00019122 | ASUI=1-ASAI
| 6713.975 | ENS=total ENS*1000
| 5.1646 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 1.6775 | 1.3235 | 0.545 | 0.91424 | 278.85 | 369.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.545 | 1.4729 | 278.85 | 594.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.545 | 1.4729 | 278.85 | 594.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.545 | 1.4729 | 278.85 | 594.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.5 | 1.3512 | 253.5 | 540.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 1.6775 | 1.3235 | 0.5 | 0.83875 | 253.5 | 335.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.415 | 1.1215 | 12.675 | 27.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 2.7025 | 2.1321 | 0.415 | 1.1215 | 12.675 | 27.025
[10 empty] | Total | 9.7659 | 1647.75 | 3082.75
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1647.75 | total F
| 1.2675 | SAIFI=total F/total customers
| 2.3713 | SAIDI=total G/total customers
| 1.8709 | CAIDI=SAIDI/SAIFI
| 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0002707 | ASUI=1-ASAI
| 9765.9 | ENS=total ENS*1000
| 7.5122 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.545 | 0.64583 | 70.4 | 260.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.545 | 0.65809 | 72.05 | 265.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.5 | 0.5925 | 64 | 237
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.5 | 0.60375 | 65.5 | 241.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.3275 |  | 1.2075 | 3.687 | 0.415 | 0.50111 | 3.275 | 12.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.185 | 3.7031 | 0.415 | 0.49178 | 3.2 | 11.85
[10 empty] | Total | 4.8092 | 422.525 | 1560.075
| 1300 | total customers
| 11388000 | total (customers*8760)
| 422.525 | total F
| 0.32502 | SAIFI=total F/total customers
| 1.2001 | SAIDI=total G/total customers
| 3.6923 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013699 | ASUI=1-ASAI
| 4809.225 | ENS=total ENS*1000
| 3.6994 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 1.7775 | 1.4024 | 0.545 | 0.96874 | 278.85 | 391.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 3.9462 | 3.1134 | 0.545 | 2.1507 | 278.85 | 868.175
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 38 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 3.9462 | 3.1134 | 0.545 | 2.1507 | 278.85 | 868.175
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 6.115 | 4.8245 | 0.545 | 3.3327 | 278.85 | 1345.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 6.115 | 4.8245 | 0.5 | 3.0575 | 253.5 | 1223
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 43 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.2675 |  | 7.2588 | 5.7268 | 0.5 | 3.6294 | 253.5 | 1451.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.415 | 3.902 | 12.675 | 94.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 33 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 36 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 39 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 41 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 32 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 34 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 35 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 37 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 38 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 40 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 42 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 43 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.2675 |  | 9.4025 | 7.4181 | 0.415 | 3.902 | 12.675 | 94.025
[10 empty] | Total | 23.0938 | 1647.75 | 6335.5
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1647.75 | total F
| 1.2675 | SAIFI=total F/total customers
| 4.8735 | SAIDI=total G/total customers
| 3.8449 | CAIDI=SAIDI/SAIFI
| 0.99944 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00055633 | ASUI=1-ASAI
| 23093.775 | ENS=total ENS*1000
| 17.7644 | AENS=ENS/total customers

## F5_(26-28)
CASE A & E
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.05 | 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
0.05 |  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
0.05 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | Calculation |  |  | 0.145 |  | 0.16625 | 1.1466 | 1 | 0.16625 | 0.145 | 0.16625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.17375 | 1.178 | 1 | 0.17375 | 0.1475 | 0.17375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.1375 |  | 0.14375 | 1.0455 | 1 | 0.14375 | 0.1375 | 0.14375
[10 empty] | Total | 0.48375 | 0.43 | 0.48375
| 3 | total customers
| 26280 | total (customers*8760)
| 0.43 | total F
| 0.14333 | SAIFI=total F/total customers
| 0.16125 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.8408e-05 | ASUI=1-ASAI
| 483.75 | ENS=total ENS*1000
| 161.25 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
[10 empty] | Total | 1.935 | 0.645 | 1.935
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.645 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.363e-05 | ASUI=1-ASAI
| 1935 | ENS=total ENS*1000
| 645 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.145 |  | 0.435 | 3 | 1 | 0.435 | 0.145 | 0.435
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.4425 | 3 | 1 | 0.4425 | 0.1475 | 0.4425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.1375 |  | 0.4125 | 3 | 1 | 0.4125 | 0.1375 | 0.4125
[10 empty] | Total | 1.29 | 0.43 | 1.29
| 3 | total customers
| 26280 | total (customers*8760)
| 0.43 | total F
| 0.14333 | SAIFI=total F/total customers
| 0.43 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.9087e-05 | ASUI=1-ASAI
| 1290 | ENS=total ENS*1000
| 430 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 49 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.20125 | 0.93605 | 1 | 0.20125 | 0.215 | 0.20125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.2075 | 0.96512 | 1 | 0.2075 | 0.215 | 0.2075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 47 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.1825 | 0.84884 | 1 | 0.1825 | 0.215 | 0.1825
[10 empty] | Total | 0.59125 | 0.645 | 0.59125
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.19708 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.2498e-05 | ASUI=1-ASAI
| 591.25 | ENS=total ENS*1000
| 197.0833 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 49 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.30125 | 1.4012 | 1 | 0.30125 | 0.215 | 0.30125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.47625 | 2.2151 | 1 | 0.47625 | 0.215 | 0.47625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 46 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 48 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 45 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 47 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 49 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
[10 empty] | Total | 1.4225 | 0.645 | 1.4225
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.47417 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.4129e-05 | ASUI=1-ASAI
| 1422.5 | ENS=total ENS*1000
| 474.1667 | AENS=ENS/total customers

## F6_(29-31)
CASE A & E
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.05 | 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
0.05 |  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
0.05 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
0.05 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | Calculation |  |  | 0.1475 |  | 0.14875 | 1.0085 | 1 | 0.14875 | 0.1475 | 0.14875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.155 |  | 0.17125 | 1.1048 | 1 | 0.17125 | 0.155 | 0.17125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.1475 |  | 0.14875 | 1.0085 | 1.5 | 0.22312 | 0.1475 | 0.14875
[10 empty] | Total | 0.54312 | 0.45 | 0.46875
| 3 | total customers
| 26280 | total (customers*8760)
| 0.45 | total F
| 0.15 | SAIFI=total F/total customers
| 0.15625 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 1.7837e-05 | ASUI=1-ASAI
| 543.125 | ENS=total ENS*1000
| 181.0417 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1 | 0.645 | 0.215 | 0.645
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1.5 | 0.9675 | 0.215 | 0.645
[10 empty] | Total | 2.2575 | 0.645 | 1.935
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.645 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.363e-05 | ASUI=1-ASAI
| 2257.5 | ENS=total ENS*1000
| 752.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.1475 |  | 0.4425 | 3 | 1 | 0.4425 | 0.1475 | 0.4425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.155 |  | 0.465 | 3 | 1 | 0.465 | 0.155 | 0.465
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.1475 |  | 0.4425 | 3 | 1.5 | 0.66375 | 0.1475 | 0.4425
[10 empty] | Total | 1.5713 | 0.45 | 1.35
| 3 | total customers
| 26280 | total (customers*8760)
| 0.45 | total F
| 0.15 | SAIFI=total F/total customers
| 0.45 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.137e-05 | ASUI=1-ASAI
| 1571.25 | ENS=total ENS*1000
| 523.75 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 55 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.1825 | 0.84884 | 1 | 0.1825 | 0.215 | 0.1825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.20125 | 0.93605 | 1 | 0.20125 | 0.215 | 0.20125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.1825 | 0.84884 | 1.5 | 0.27375 | 0.215 | 0.1825
[10 empty] | Total | 0.6575 | 0.645 | 0.56625
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.18875 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99998 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.1547e-05 | ASUI=1-ASAI
| 657.5 | ENS=total ENS*1000
| 219.1667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 55 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.27625 | 1.2849 | 1 | 0.27625 | 0.215 | 0.27625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | Calculation |  |  | 0.215 |  | 0.47 | 2.186 | 1 | 0.47 | 0.215 | 0.47
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 52 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 54 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 51 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 53 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 55 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | Calculation |  |  | 0.215 |  | 0.645 | 3 | 1.5 | 0.9675 | 0.215 | 0.645
[10 empty] | Total | 1.7138 | 0.645 | 1.3913
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.46375 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.2939e-05 | ASUI=1-ASAI
| 1713.75 | ENS=total ENS*1000
| 571.25 | AENS=ENS/total customers

## F7_(32-38)
CASE A
0.05 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.05 | 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
0.05 |  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
0.05 |  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
0.05 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.05 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.05 |  |  | x former |  |  | 0.1 | 10 | 1
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | x former |  |  | 0 | 0 | 0
0.05 |  |  | Calculation |  |  | 0.32 |  | 1.21 | 3.7812 | 0.545 | 0.65945 | 70.4 | 266.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.21 | 3.7812 | 0.545 | 0.65945 | 70.4 | 266.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.31 |  | 1.18 | 3.8065 | 0.545 | 0.6431 | 68.2 | 259.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.21 | 3.4571 | 0.545 | 0.65945 | 77 | 266.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.18 | 3.3714 | 0.5 | 0.59 | 70 | 236
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.21 | 3.4571 | 0.5 | 0.605 | 70 | 242
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.18 | 3.3714 | 0.415 | 0.4897 | 3.5 | 11.8
[10 empty] | Total | 4.3061 | 429.5 | 1548
| 1290 | total customers
| 11300400 | total (customers*8760)
| 429.5 | total F
| 0.33295 | SAIFI=total F/total customers
| 1.2 | SAIDI=total G/total customers
| 3.6042 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013699 | ASUI=1-ASAI
| 4306.15 | ENS=total ENS*1000
| 3.3381 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.545 | 4.518 | 248.6 | 1823.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.545 | 4.518 | 248.6 | 1823.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.545 | 4.518 | 248.6 | 1823.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.545 | 4.518 | 248.6 | 1823.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.5 | 4.145 | 226 | 1658
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.5 | 4.145 | 226 | 1658
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.415 | 3.4403 | 11.3 | 82.9
[10 empty] | Total | 29.8025 | 1457.7 | 10694.1
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1457.7 | total F
| 1.13 | SAIFI=total F/total customers
| 8.29 | SAIDI=total G/total customers
| 7.3363 | CAIDI=SAIDI/SAIFI
| 0.99905 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00094635 | ASUI=1-ASAI
| 29802.55 | ENS=total ENS*1000
| 23.1028 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.545 | 0.9047 | 70.4 | 365.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.66 | 5.1875 | 0.545 | 0.9047 | 70.4 | 365.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.31 |  | 1.63 | 5.2581 | 0.545 | 0.88835 | 68.2 | 358.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.75 | 5 | 0.545 | 0.95375 | 77 | 385
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.75 | 5 | 0.5 | 0.875 | 70 | 350
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.75 | 5 | 0.5 | 0.875 | 70 | 350
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.75 | 5 | 0.415 | 0.72625 | 3.5 | 17.5
[10 empty] | Total | 6.1278 | 429.5 | 2191.5
| 1290 | total customers
| 11300400 | total (customers*8760)
| 429.5 | total F
| 0.33295 | SAIFI=total F/total customers
| 1.6988 | SAIDI=total G/total customers
| 5.1024 | CAIDI=SAIDI/SAIFI
| 0.99981 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00019393 | ASUI=1-ASAI
| 6127.75 | ENS=total ENS*1000
| 4.7502 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 1.615 | 1.4292 | 0.545 | 0.88018 | 248.6 | 355.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 1.615 | 1.4292 | 0.545 | 0.88018 | 248.6 | 355.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 2.64 | 2.3363 | 0.545 | 1.4388 | 248.6 | 580.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 2.64 | 2.3363 | 0.545 | 1.4388 | 248.6 | 580.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 1.59 | 1.4071 | 0.5 | 0.795 | 226 | 318
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 2.64 | 2.3363 | 0.5 | 1.32 | 226 | 528
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 2.64 | 2.3363 | 0.415 | 1.0956 | 11.3 | 26.4
[10 empty] | Total | 7.8485 | 1457.7 | 2744.6
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1457.7 | total F
| 1.13 | SAIFI=total F/total customers
| 2.1276 | SAIDI=total G/total customers
| 1.8828 | CAIDI=SAIDI/SAIFI
| 0.99976 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00024288 | ASUI=1-ASAI
| 7848.55 | ENS=total ENS*1000
| 6.0841 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.21 | 3.7812 | 0.545 | 0.65945 | 70.4 | 266.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.32 |  | 1.21 | 3.7812 | 0.545 | 0.65945 | 70.4 | 266.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.31 |  | 1.18 | 3.8065 | 0.545 | 0.6431 | 68.2 | 259.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.21 | 3.4571 | 0.545 | 0.65945 | 77 | 266.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.18 | 3.3714 | 0.5 | 0.59 | 70 | 236
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.21 | 3.4571 | 0.5 | 0.605 | 70 | 242
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0 | 0
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.35 |  | 1.18 | 3.3714 | 0.415 | 0.4897 | 3.5 | 11.8
[10 empty] | Total | 4.3061 | 429.5 | 1548
| 1290 | total customers
| 11300400 | total (customers*8760)
| 429.5 | total F
| 0.33295 | SAIFI=total F/total customers
| 1.2 | SAIDI=total G/total customers
| 3.6042 | CAIDI=SAIDI/SAIFI
| 0.99986 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00013699 | ASUI=1-ASAI
| 4306.15 | ENS=total ENS*1000
| 3.3381 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 1.7088 | 1.5122 | 0.545 | 0.93127 | 248.6 | 375.925
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 62 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 2.8337 | 2.5077 | 0.545 | 1.5444 | 248.6 | 623.425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 5.0025 | 4.427 | 0.545 | 2.7264 | 248.6 | 1100.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 5.0025 | 4.427 | 0.545 | 2.7264 | 248.6 | 1100.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 0.5 | 0.01875
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 0.5 | 0.02
|  |  | 67 | 0.6 | 0.05 | 0.03 | 0.5 | 0.015
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.13 |  | 6.1212 | 5.417 | 0.5 | 3.0606 | 226 | 1224.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.5 | 4.145 | 226 | 1658
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 58 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 60 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 63 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 65 | 0.75 | 0.05 | 0.0375 | 3 | 0.1125
|  |  | 57 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 59 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 61 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 62 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 64 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | 66 | 0.8 | 0.05 | 0.04 | 3 | 0.12
|  |  | 67 | 0.6 | 0.05 | 0.03 | 3 | 0.09
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.13 |  | 8.29 | 7.3363 | 0.415 | 3.4403 | 11.3 | 82.9
[10 empty] | Total | 18.5744 | 1457.7 | 6165.6
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1457.7 | total F
| 1.13 | SAIFI=total F/total customers
| 4.7795 | SAIDI=total G/total customers
| 4.2297 | CAIDI=SAIDI/SAIFI
| 0.99945 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00054561 | ASUI=1-ASAI
| 18574.3625 | ENS=total ENS*1000
| 14.3987 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 4212.225 | 1100 | 29176.875 | 1100 | 5835.6 | 1100 | 7608.1875 | 1100 | 4212.225 | 1100 | 17938.4688 | 1100
Feeder 2 | 571.25 | 3 | 2283.75 | 3 | 1533.75 | 3 | 696.25 | 3 | 571.25 | 3 | 1652.5 | 3
Feeder 3 | 4145.8313 | 1080 | 28698.8625 | 1080 | 5868.7215 | 1080 | 7495.2688 | 1080 | 4145.8313 | 1080 | 18584.5187 | 1080
Feeder 4 | 4809.225 | 1300 | 37704.025 | 1300 | 6713.975 | 1300 | 9765.9 | 1300 | 4809.225 | 1300 | 23093.775 | 1300
Feeder 5 | 483.75 | 3 | 1935 | 3 | 1290 | 3 | 591.25 | 3 | 483.75 | 3 | 1422.5 | 3
Feeder 6 | 543.125 | 3 | 2257.5 | 3 | 1571.25 | 3 | 657.5 | 3 | 543.125 | 3 | 571.25 | 3
Feeder 7 | 4306.15 | 1290 | 29802.55 | 1290 | 6127.75 | 1290 | 7848.55 | 1290 | 4306.15 | 1290 | 18574.3625 | 1290
TOTAL | 19071.5563 | 4779 | 131858.5625 | 4779 | 28941.0465 | 4779 | 34662.9062 | 4779 | 19071.5563 | 4779 | 81837.375 | 4779
Analytic | 19.0716 |  | 131.8586 |  | 28.941 |  | 34.6629 |  | 19.0716 |  | 81.8374
Monte Carlo_Code | 19.066 |  | 131.83 |  | 28.573 |  | 34.66 |  | 19.065 |  | 81.951
Deviation | 0.029134 |  | 0.021661 |  | 1.2717 |  | 0.0083843 |  | 0.034377 |  | -0.13884
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 19.072 | 19.066 | 19.078 | 19.037 |  | 945000 | 131.83 | 131.96 | 131.96 | 131.9
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 28.532 | 28.541 | 28.573 | 28.523 |  | 47500 | 34.672 | 38.847 | 34.66 | 34.664
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 19.039 | 19.065 | 19.048 | 19.042 |  | 1140000 | 81.951 | 82.068 | 82.097 | 81.987