## F1_(1-7)
CASE A
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.075 | 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
0.075 |  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
0.075 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | Calculation |  |  | 0.4225 |  | 1.2737 | 3.0148 | 0.545 | 0.69419 | 92.95 | 280.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43375 |  | 1.3075 | 3.0144 | 0.545 | 0.71259 | 95.425 | 287.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.2737 | 3.0148 | 0.545 | 0.69419 | 92.95 | 280.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3188 | 2.6709 | 0.545 | 0.71872 | 108.625 | 290.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3075 | 2.6481 | 0.5 | 0.65375 | 98.75 | 261.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3188 | 2.6709 | 0.415 | 0.54728 | 4.9375 | 13.1875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3075 | 2.6481 | 0.415 | 0.54261 | 4.9375 | 13.075
[10 empty] | Total | 4.5633 | 498.575 | 1425.9875
| 1100 | total customers
| 9636000 | total (customers*8760)
| 498.575 | total F
| 0.45325 | SAIFI=total F/total customers
| 1.2964 | SAIDI=total G/total customers
| 2.8601 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014799 | ASUI=1-ASAI
| 4563.3375 | ENS=total ENS*1000
| 4.1485 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.545 | 4.888 | 298.375 | 1973.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.545 | 4.888 | 298.375 | 1973.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.545 | 4.888 | 298.375 | 1973.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.545 | 4.888 | 298.375 | 1973.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.5 | 4.4844 | 271.25 | 1793.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.415 | 3.722 | 13.5625 | 89.6875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.415 | 3.722 | 13.5625 | 89.6875
[10 empty] | Total | 31.4803 | 1491.875 | 9865.625
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1491.875 | total F
| 1.3563 | SAIFI=total F/total customers
| 8.9688 | SAIDI=total G/total customers
| 6.6129 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010238 | ASUI=1-ASAI
| 31480.3125 | ENS=total ENS*1000
| 28.6185 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.9675 | 4.6568 | 0.545 | 1.0723 | 92.95 | 432.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43375 |  | 2.0012 | 4.6138 | 0.545 | 1.0907 | 95.425 | 440.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.9675 | 4.6568 | 0.545 | 1.0723 | 92.95 | 432.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 2.0125 | 4.0759 | 0.545 | 1.0968 | 108.625 | 442.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 2.0012 | 4.0532 | 0.5 | 1.0006 | 98.75 | 400.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 2.0125 | 4.0759 | 0.415 | 0.83519 | 4.9375 | 20.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 2.0012 | 4.0532 | 0.415 | 0.83052 | 4.9375 | 20.0125
[10 empty] | Total | 6.9984 | 498.575 | 2189.1125
| 1100 | total customers
| 9636000 | total (customers*8760)
| 498.575 | total F
| 0.45325 | SAIFI=total F/total customers
| 1.9901 | SAIDI=total G/total customers
| 4.3907 | CAIDI=SAIDI/SAIFI
| 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022718 | ASUI=1-ASAI
| 6998.4 | ENS=total ENS*1000
| 6.3622 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 1.7406 | 1.2834 | 0.545 | 0.94864 | 298.375 | 382.9375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 1.7688 | 1.3041 | 0.545 | 0.96397 | 298.375 | 389.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 1.7406 | 1.2834 | 0.545 | 0.94864 | 298.375 | 382.9375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 2.8687 | 2.1152 | 0.545 | 1.5635 | 298.375 | 631.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 2.8687 | 2.1152 | 0.5 | 1.4344 | 271.25 | 573.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 2.8687 | 2.1152 | 0.415 | 1.1905 | 13.5625 | 28.6875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 2.8687 | 2.1152 | 0.415 | 1.1905 | 13.5625 | 28.6875
[10 empty] | Total | 8.2402 | 1491.875 | 2417.25
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1491.875 | total F
| 1.3563 | SAIFI=total F/total customers
| 2.1975 | SAIDI=total G/total customers
| 1.6203 | CAIDI=SAIDI/SAIFI
| 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00025086 | ASUI=1-ASAI
| 8240.1562 | ENS=total ENS*1000
| 7.4911 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.2737 | 3.0148 | 0.545 | 0.69419 | 92.95 | 280.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43375 |  | 1.3075 | 3.0144 | 0.545 | 0.71259 | 95.425 | 287.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.2737 | 3.0148 | 0.545 | 0.69419 | 92.95 | 280.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3188 | 2.6709 | 0.545 | 0.71872 | 108.625 | 290.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3075 | 2.6481 | 0.5 | 0.65375 | 98.75 | 261.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3188 | 2.6709 | 0.415 | 0.54728 | 4.9375 | 13.1875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.49375 |  | 1.3075 | 2.6481 | 0.415 | 0.54261 | 4.9375 | 13.075
[10 empty] | Total | 4.5633 | 498.575 | 1425.9875
| 1100 | total customers
| 9636000 | total (customers*8760)
| 498.575 | total F
| 0.45325 | SAIFI=total F/total customers
| 1.2964 | SAIDI=total G/total customers
| 2.8601 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014799 | ASUI=1-ASAI
| 4563.3375 | ENS=total ENS*1000
| 4.1485 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 1.8813 | 1.3871 | 0.545 | 1.0253 | 298.375 | 413.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 3.1219 | 2.3018 | 0.545 | 1.7014 | 298.375 | 686.8125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 4.3344 | 3.1959 | 0.545 | 2.3622 | 298.375 | 953.5625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 6.6656 | 4.9147 | 0.545 | 3.6328 | 298.375 | 1466.4375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3563 |  | 6.6656 | 4.9147 | 0.5 | 3.3328 | 271.25 | 1333.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.415 | 3.722 | 13.5625 | 89.6875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 3 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 5 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 7 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 10 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 2 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 4 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 6 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 8 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 9 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 11 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 12 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3563 |  | 8.9688 | 6.6129 | 0.415 | 3.722 | 13.5625 | 89.6875
[10 empty] | Total | 19.4986 | 1491.875 | 5033.1875
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1491.875 | total F
| 1.3563 | SAIFI=total F/total customers
| 4.5756 | SAIDI=total G/total customers
| 3.3737 | CAIDI=SAIDI/SAIFI
| 0.99948 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00052233 | ASUI=1-ASAI
| 19498.5781 | ENS=total ENS*1000
| 17.726 | AENS=ENS/total customers

## F2_(8-10)
CASE A & E
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.075 | 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
0.075 |  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
0.075 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | Calculation |  |  | 0.21 |  | 0.2175 | 1.0357 | 1 | 0.2175 | 0.21 | 0.2175
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.25125 | 1.1356 | 1.5 | 0.37687 | 0.22125 | 0.25125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.225 |  | 0.2625 | 1.1667 | 1 | 0.2625 | 0.225 | 0.2625
[10 empty] | Total | 0.85687 | 0.65625 | 0.73125
| 3 | total customers
| 26280 | total (customers*8760)
| 0.65625 | total F
| 0.21875 | SAIFI=total F/total customers
| 0.24375 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.7825e-05 | ASUI=1-ASAI
| 856.875 | ENS=total ENS*1000
| 285.625 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.97875 | 3 | 1 | 0.97875 | 0.32625 | 0.97875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.97875 | 3 | 1.5 | 1.4681 | 0.32625 | 0.97875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.97875 | 3 | 1 | 0.97875 | 0.32625 | 0.97875
[10 empty] | Total | 3.4256 | 0.97875 | 2.9363
| 3 | total customers
| 26280 | total (customers*8760)
| 0.97875 | total F
| 0.32625 | SAIFI=total F/total customers
| 0.97875 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00011173 | ASUI=1-ASAI
| 3425.625 | ENS=total ENS*1000
| 1141.875 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.21 |  | 0.63 | 3 | 1 | 0.63 | 0.21 | 0.63
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.66375 | 3 | 1.5 | 0.99562 | 0.22125 | 0.66375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.225 |  | 0.675 | 3 | 1 | 0.675 | 0.225 | 0.675
[10 empty] | Total | 2.3006 | 0.65625 | 1.9688
| 3 | total customers
| 26280 | total (customers*8760)
| 0.65625 | total F
| 0.21875 | SAIFI=total F/total customers
| 0.65625 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.4914e-05 | ASUI=1-ASAI
| 2300.625 | ENS=total ENS*1000
| 766.875 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 18 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.32625 |  | 0.27563 | 0.84483 | 1 | 0.27563 | 0.32625 | 0.27563
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.32625 |  | 0.30375 | 0.93103 | 1.5 | 0.45562 | 0.32625 | 0.30375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.31312 | 0.95977 | 1 | 0.31312 | 0.32625 | 0.31312
[10 empty] | Total | 1.0444 | 0.97875 | 0.8925
| 3 | total customers
| 26280 | total (customers*8760)
| 0.97875 | total F
| 0.32625 | SAIFI=total F/total customers
| 0.2975 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.3961e-05 | ASUI=1-ASAI
| 1044.375 | ENS=total ENS*1000
| 348.125 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 18 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.32625 |  | 0.42563 | 1.3046 | 1 | 0.42563 | 0.32625 | 0.42563
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.32625 |  | 0.71625 | 2.1954 | 1.5 | 1.0744 | 0.32625 | 0.71625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 15 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 17 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 14 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 16 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 18 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.32625 |  | 0.97875 | 3 | 1 | 0.97875 | 0.32625 | 0.97875
[10 empty] | Total | 2.4787 | 0.97875 | 2.1206
| 3 | total customers
| 26280 | total (customers*8760)
| 0.97875 | total F
| 0.32625 | SAIFI=total F/total customers
| 0.70688 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 8.0693e-05 | ASUI=1-ASAI
| 2478.75 | ENS=total ENS*1000
| 826.25 | AENS=ENS/total customers

## F3_(11-17)
CASE A
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.075 | 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
0.075 |  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
0.075 |  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
0.075 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | Calculation |  |  | 0.42625 |  | 1.3131 | 3.0806 | 0.545 | 0.71565 | 93.775 | 288.8875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.3019 | 3.0814 | 0.545 | 0.70952 | 92.95 | 286.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.3019 | 3.0814 | 0.545 | 0.70952 | 92.95 | 286.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.2681 | 2.7126 | 0.5 | 0.63406 | 93.5 | 253.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.3019 | 2.7848 | 0.5 | 0.65094 | 93.5 | 260.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.3019 | 2.7848 | 0.415 | 0.54028 | 4.675 | 13.0187
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.2681 | 2.7126 | 0.415 | 0.52627 | 4.675 | 12.6812
[10 empty] | Total | 4.4862 | 476.025 | 1401.4125
| 1080 | total customers
| 9460800 | total (customers*8760)
| 476.025 | total F
| 0.44076 | SAIFI=total F/total customers
| 1.2976 | SAIDI=total G/total customers
| 2.944 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014813 | ASUI=1-ASAI
| 4486.2469 | ENS=total ENS*1000
| 4.1539 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.545 | 4.8634 | 295.075 | 1963.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.545 | 4.8634 | 295.075 | 1963.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.545 | 4.8634 | 295.075 | 1963.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.5 | 4.4619 | 268.25 | 1784.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.5 | 4.4619 | 268.25 | 1784.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.415 | 3.7034 | 13.4125 | 89.2375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.415 | 3.7034 | 13.4125 | 89.2375
[10 empty] | Total | 30.9208 | 1448.55 | 9637.65
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1448.55 | total F
| 1.3413 | SAIFI=total F/total customers
| 8.9237 | SAIDI=total G/total customers
| 6.6533 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010187 | ASUI=1-ASAI
| 30920.7937 | ENS=total ENS*1000
| 28.6304 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.42625 |  | 1.9788 | 4.6422 | 0.545 | 1.0784 | 93.775 | 435.325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.9675 | 4.6568 | 0.545 | 1.0723 | 92.95 | 432.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.9675 | 4.6568 | 0.545 | 1.0723 | 92.95 | 432.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 2.1025 | 4.4973 | 0.5 | 1.0513 | 93.5 | 420.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 2.1025 | 4.4973 | 0.5 | 1.0513 | 93.5 | 420.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 2.1025 | 4.4973 | 0.415 | 0.87254 | 4.675 | 21.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 2.1025 | 4.4973 | 0.415 | 0.87254 | 4.675 | 21.025
[10 empty] | Total | 7.0706 | 476.025 | 2184.075
| 1080 | total customers
| 9460800 | total (customers*8760)
| 476.025 | total F
| 0.44076 | SAIFI=total F/total customers
| 2.0223 | SAIDI=total G/total customers
| 4.5882 | CAIDI=SAIDI/SAIFI
| 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023086 | ASUI=1-ASAI
| 7070.5687 | ENS=total ENS*1000
| 6.5468 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 1.7706 | 1.3201 | 0.545 | 0.96499 | 295.075 | 389.5375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 1.7613 | 1.3131 | 0.545 | 0.95988 | 295.075 | 387.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 2.8237 | 2.1053 | 0.545 | 1.5389 | 295.075 | 621.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 2.8237 | 2.1053 | 0.5 | 1.4119 | 268.25 | 564.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 1.7613 | 1.3131 | 0.5 | 0.88063 | 268.25 | 352.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 2.8237 | 2.1053 | 0.415 | 1.1719 | 13.4125 | 28.2375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 2.8237 | 2.1053 | 0.415 | 1.1719 | 13.4125 | 28.2375
[10 empty] | Total | 8.1 | 1448.55 | 2371.7125
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1448.55 | total F
| 1.3413 | SAIFI=total F/total customers
| 2.196 | SAIDI=total G/total customers
| 1.6373 | CAIDI=SAIDI/SAIFI
| 0.99975 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00025069 | ASUI=1-ASAI
| 8100.0281 | ENS=total ENS*1000
| 7.5 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.42625 |  | 1.3131 | 3.0806 | 0.545 | 0.71565 | 93.775 | 288.8875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.3019 | 3.0814 | 0.545 | 0.70952 | 92.95 | 286.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4225 |  | 1.3019 | 3.0814 | 0.545 | 0.70952 | 92.95 | 286.4125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.2681 | 2.7126 | 0.5 | 0.63406 | 93.5 | 253.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.3019 | 2.7848 | 0.5 | 0.65094 | 93.5 | 260.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.3019 | 2.7848 | 0.415 | 0.54028 | 4.675 | 13.0187
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0 | 0
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.4675 |  | 1.2681 | 2.7126 | 0.415 | 0.52627 | 4.675 | 12.6812
[10 empty] | Total | 4.4862 | 476.025 | 1401.4125
| 1080 | total customers
| 9460800 | total (customers*8760)
| 476.025 | total F
| 0.44076 | SAIFI=total F/total customers
| 1.2976 | SAIDI=total G/total customers
| 2.944 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014813 | ASUI=1-ASAI
| 4486.2469 | ENS=total ENS*1000
| 4.1539 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 1.9113 | 1.425 | 0.545 | 1.0416 | 295.075 | 420.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 25 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 3.1144 | 2.322 | 0.545 | 1.6973 | 295.075 | 685.1625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 5.4175 | 4.0391 | 0.545 | 2.9525 | 295.075 | 1191.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.3413 |  | 5.4175 | 4.0391 | 0.5 | 2.7087 | 268.25 | 1083.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 30 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.5581 | 6.3807 | 0.5 | 4.2791 | 268.25 | 1711.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.415 | 3.7034 | 13.4125 | 89.2375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 21 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 23 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 26 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 28 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 20 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 22 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 24 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 25 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 27 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 29 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 30 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.3413 |  | 8.9238 | 6.6533 | 0.415 | 3.7034 | 13.4125 | 89.2375
[10 empty] | Total | 20.086 | 1448.55 | 5271.0875
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1448.55 | total F
| 1.3413 | SAIFI=total F/total customers
| 4.8806 | SAIDI=total G/total customers
| 3.6389 | CAIDI=SAIDI/SAIFI
| 0.99944 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00055715 | ASUI=1-ASAI
| 20086.0281 | ENS=total ENS*1000
| 18.5982 | AENS=ENS/total customers

## F4_(18-25)
CASE A
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.075 | 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
0.075 |  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
0.075 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.545 | 0.69624 | 94.6 | 281.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.5 | 0.63875 | 86 | 255.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.5 | 0.65563 | 88.25 | 262.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.415 | 0.54417 | 4.4125 | 13.1125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.415 | 0.53016 | 4.3 | 12.775
[10 empty] | Total | 5.2088 | 568.7875 | 1690.1125
| 1300 | total customers
| 11388000 | total (customers*8760)
| 568.7875 | total F
| 0.43753 | SAIFI=total F/total customers
| 1.3001 | SAIDI=total G/total customers
| 2.9714 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014841 | ASUI=1-ASAI
| 5208.8375 | ENS=total ENS*1000
| 4.0068 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.545 | 5.5065 | 330.275 | 2222.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.545 | 5.5065 | 330.275 | 2222.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.545 | 5.5065 | 330.275 | 2222.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.545 | 5.5065 | 330.275 | 2222.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.5 | 5.0519 | 300.25 | 2020.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.5 | 5.0519 | 300.25 | 2020.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.415 | 4.1931 | 15.0125 | 101.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.415 | 4.1931 | 15.0125 | 101.0375
[10 empty] | Total | 40.516 | 1951.625 | 13134.875
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1951.625 | total F
| 1.5013 | SAIFI=total F/total customers
| 10.1037 | SAIDI=total G/total customers
| 6.7302 | CAIDI=SAIDI/SAIFI
| 0.99885 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0011534 | ASUI=1-ASAI
| 40516.0375 | ENS=total ENS*1000
| 31.1662 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.545 | 1.1029 | 97.075 | 445.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.545 | 1.0846 | 94.6 | 437.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.545 | 1.1029 | 97.075 | 445.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.545 | 1.1029 | 97.075 | 445.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.5 | 0.995 | 86 | 398
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.5 | 1.0119 | 88.25 | 404.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 2.0237 | 4.5864 | 0.415 | 0.83986 | 4.4125 | 20.2375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.415 | 0.82585 | 4.3 | 19.9
[10 empty] | Total | 8.066 | 568.7875 | 2616.3625
| 1300 | total customers
| 11388000 | total (customers*8760)
| 568.7875 | total F
| 0.43753 | SAIFI=total F/total customers
| 2.0126 | SAIDI=total G/total customers
| 4.5999 | CAIDI=SAIDI/SAIFI
| 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022975 | ASUI=1-ASAI
| 8065.9625 | ENS=total ENS*1000
| 6.2046 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 1.8413 | 1.2265 | 0.545 | 1.0035 | 330.275 | 405.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.545 | 1.5825 | 330.275 | 638.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.545 | 1.5825 | 330.275 | 638.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.545 | 1.5825 | 330.275 | 638.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.5 | 1.4519 | 300.25 | 580.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 1.8413 | 1.2265 | 0.5 | 0.92063 | 300.25 | 368.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.415 | 1.2051 | 15.0125 | 29.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 2.9037 | 1.9342 | 0.415 | 1.2051 | 15.0125 | 29.0375
[10 empty] | Total | 10.5337 | 1951.625 | 3328.625
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1951.625 | total F
| 1.5013 | SAIFI=total F/total customers
| 2.5605 | SAIDI=total G/total customers
| 1.7056 | CAIDI=SAIDI/SAIFI
| 0.99971 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00029229 | ASUI=1-ASAI
| 10533.725 | ENS=total ENS*1000
| 8.1029 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.545 | 0.69624 | 94.6 | 281.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.545 | 0.71463 | 97.075 | 288.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.5 | 0.63875 | 86 | 255.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.5 | 0.65563 | 88.25 | 262.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.44125 |  | 1.3113 | 2.9717 | 0.415 | 0.54417 | 4.4125 | 13.1125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.2775 | 2.9709 | 0.415 | 0.53016 | 4.3 | 12.775
[10 empty] | Total | 5.2088 | 568.7875 | 1690.1125
| 1300 | total customers
| 11388000 | total (customers*8760)
| 568.7875 | total F
| 0.43753 | SAIFI=total F/total customers
| 1.3001 | SAIDI=total G/total customers
| 2.9714 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014841 | ASUI=1-ASAI
| 5208.8375 | ENS=total ENS*1000
| 4.0068 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 1.9913 | 1.3264 | 0.545 | 1.0852 | 330.275 | 438.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 4.2944 | 2.8605 | 0.545 | 2.3404 | 330.275 | 944.7625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 38 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 4.2944 | 2.8605 | 0.545 | 2.3404 | 330.275 | 944.7625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 6.5975 | 4.3947 | 0.545 | 3.5956 | 330.275 | 1451.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 6.5975 | 4.3947 | 0.5 | 3.2987 | 300.25 | 1319.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 43 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.5013 |  | 7.8381 | 5.2211 | 0.5 | 3.9191 | 300.25 | 1567.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.415 | 4.1931 | 15.0125 | 101.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 33 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 36 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 39 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 41 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 32 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 34 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 35 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 37 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 38 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 40 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 42 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 43 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.5013 |  | 10.1037 | 6.7302 | 0.415 | 4.1931 | 15.0125 | 101.0375
[10 empty] | Total | 24.9657 | 1951.625 | 6868.25
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1951.625 | total F
| 1.5013 | SAIFI=total F/total customers
| 5.2833 | SAIDI=total G/total customers
| 3.5192 | CAIDI=SAIDI/SAIFI
| 0.9994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00060311 | ASUI=1-ASAI
| 24965.6625 | ENS=total ENS*1000
| 19.2044 | AENS=ENS/total customers

## F5_(26-28)
CASE A & E
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.075 | 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
0.075 |  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
0.075 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | Calculation |  |  | 0.2175 |  | 0.24937 | 1.1466 | 1 | 0.24937 | 0.2175 | 0.24937
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.26062 | 1.178 | 1 | 0.26062 | 0.22125 | 0.26062
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.20625 |  | 0.21563 | 1.0455 | 1 | 0.21563 | 0.20625 | 0.21563
[10 empty] | Total | 0.72562 | 0.645 | 0.72562
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.24187 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.7611e-05 | ASUI=1-ASAI
| 725.625 | ENS=total ENS*1000
| 241.875 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
[10 empty] | Total | 2.9025 | 0.9675 | 2.9025
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.9675 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00011045 | ASUI=1-ASAI
| 2902.5 | ENS=total ENS*1000
| 967.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.2175 |  | 0.6525 | 3 | 1 | 0.6525 | 0.2175 | 0.6525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.66375 | 3 | 1 | 0.66375 | 0.22125 | 0.66375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.20625 |  | 0.61875 | 3 | 1 | 0.61875 | 0.20625 | 0.61875
[10 empty] | Total | 1.935 | 0.645 | 1.935
| 3 | total customers
| 26280 | total (customers*8760)
| 0.645 | total F
| 0.215 | SAIFI=total F/total customers
| 0.645 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.363e-05 | ASUI=1-ASAI
| 1935 | ENS=total ENS*1000
| 645 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 49 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.30188 | 0.93605 | 1 | 0.30188 | 0.3225 | 0.30188
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.31125 | 0.96512 | 1 | 0.31125 | 0.3225 | 0.31125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 47 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.27375 | 0.84884 | 1 | 0.27375 | 0.3225 | 0.27375
[10 empty] | Total | 0.88688 | 0.9675 | 0.88688
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.29563 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.3747e-05 | ASUI=1-ASAI
| 886.875 | ENS=total ENS*1000
| 295.625 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 49 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.45187 | 1.4012 | 1 | 0.45187 | 0.3225 | 0.45187
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.71437 | 2.2151 | 1 | 0.71437 | 0.3225 | 0.71437
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 46 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 48 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 45 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 47 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 49 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
[10 empty] | Total | 2.1338 | 0.9675 | 2.1338
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.71125 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 8.1193e-05 | ASUI=1-ASAI
| 2133.75 | ENS=total ENS*1000
| 711.25 | AENS=ENS/total customers

## F6_(29-31)
CASE A & E
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.075 | 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
0.075 |  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
0.075 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
0.075 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | Calculation |  |  | 0.22125 |  | 0.22313 | 1.0085 | 1 | 0.22313 | 0.22125 | 0.22313
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.2325 |  | 0.25687 | 1.1048 | 1 | 0.25687 | 0.2325 | 0.25687
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.22125 |  | 0.22313 | 1.0085 | 1.5 | 0.33469 | 0.22125 | 0.22313
[10 empty] | Total | 0.81469 | 0.675 | 0.70312
| 3 | total customers
| 26280 | total (customers*8760)
| 0.675 | total F
| 0.225 | SAIFI=total F/total customers
| 0.23438 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 2.6755e-05 | ASUI=1-ASAI
| 814.6875 | ENS=total ENS*1000
| 271.5625 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1 | 0.9675 | 0.3225 | 0.9675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1.5 | 1.4512 | 0.3225 | 0.9675
[10 empty] | Total | 3.3862 | 0.9675 | 2.9025
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.9675 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00011045 | ASUI=1-ASAI
| 3386.25 | ENS=total ENS*1000
| 1128.75 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.22125 |  | 0.66375 | 3 | 1 | 0.66375 | 0.22125 | 0.66375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.2325 |  | 0.6975 | 3 | 1 | 0.6975 | 0.2325 | 0.6975
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.22125 |  | 0.66375 | 3 | 1.5 | 0.99563 | 0.22125 | 0.66375
[10 empty] | Total | 2.3569 | 0.675 | 2.025
| 3 | total customers
| 26280 | total (customers*8760)
| 0.675 | total F
| 0.225 | SAIFI=total F/total customers
| 0.675 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.7055e-05 | ASUI=1-ASAI
| 2356.875 | ENS=total ENS*1000
| 785.625 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 55 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.27375 | 0.84884 | 1 | 0.27375 | 0.3225 | 0.27375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.30188 | 0.93605 | 1 | 0.30188 | 0.3225 | 0.30188
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.27375 | 0.84884 | 1.5 | 0.41063 | 0.3225 | 0.27375
[10 empty] | Total | 0.98625 | 0.9675 | 0.84937
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.28313 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99997 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.232e-05 | ASUI=1-ASAI
| 986.25 | ENS=total ENS*1000
| 328.75 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 55 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.41438 | 1.2849 | 1 | 0.41438 | 0.3225 | 0.41438
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | Calculation |  |  | 0.3225 |  | 0.705 | 2.186 | 1 | 0.705 | 0.3225 | 0.705
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 52 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 54 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 51 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 53 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 55 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | Calculation |  |  | 0.3225 |  | 0.9675 | 3 | 1.5 | 1.4512 | 0.3225 | 0.9675
[10 empty] | Total | 2.5706 | 0.9675 | 2.0869
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9675 | total F
| 0.3225 | SAIFI=total F/total customers
| 0.69563 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99992 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 7.9409e-05 | ASUI=1-ASAI
| 2570.625 | ENS=total ENS*1000
| 856.875 | AENS=ENS/total customers

## F7_(32-38)
CASE A
0.075 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
0.075 | 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
0.075 |  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
0.075 |  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
0.075 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.075 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.075 |  |  | x former |  |  | 0.1 | 10 | 1
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | x former |  |  | 0 | 0 | 0
0.075 |  |  | Calculation |  |  | 0.43 |  | 1.315 | 3.0581 | 0.545 | 0.71668 | 94.6 | 289.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.315 | 3.0581 | 0.545 | 0.71668 | 94.6 | 289.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.415 |  | 1.27 | 3.0602 | 0.545 | 0.69215 | 91.3 | 279.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.315 | 2.7684 | 0.545 | 0.71668 | 104.5 | 289.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.27 | 2.6737 | 0.5 | 0.635 | 95 | 254
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.315 | 2.7684 | 0.5 | 0.6575 | 95 | 263
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.27 | 2.6737 | 0.415 | 0.52705 | 4.75 | 12.7
[10 empty] | Total | 4.6617 | 579.75 | 1677
| 1290 | total customers
| 11300400 | total (customers*8760)
| 579.75 | total F
| 0.44942 | SAIFI=total F/total customers
| 1.3 | SAIDI=total G/total customers
| 2.8926 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001484 | ASUI=1-ASAI
| 4661.725 | ENS=total ENS*1000
| 3.6137 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.545 | 4.8696 | 295.9 | 1965.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.545 | 4.8696 | 295.9 | 1965.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.545 | 4.8696 | 295.9 | 1965.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.545 | 4.8696 | 295.9 | 1965.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.5 | 4.4675 | 269 | 1787
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.5 | 4.4675 | 269 | 1787
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.415 | 3.708 | 13.45 | 89.35
[10 empty] | Total | 32.1213 | 1735.05 | 11526.15
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1735.05 | total F
| 1.345 | SAIFI=total F/total customers
| 8.935 | SAIDI=total G/total customers
| 6.6431 | CAIDI=SAIDI/SAIFI
| 0.99898 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00102 | ASUI=1-ASAI
| 32121.325 | ENS=total ENS*1000
| 24.9003 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.545 | 1.0845 | 94.6 | 437.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.99 | 4.6279 | 0.545 | 1.0845 | 94.6 | 437.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.415 |  | 1.945 | 4.6867 | 0.545 | 1.06 | 91.3 | 427.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 2.125 | 4.4737 | 0.545 | 1.1581 | 104.5 | 467.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 2.125 | 4.4737 | 0.5 | 1.0625 | 95 | 425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 2.125 | 4.4737 | 0.5 | 1.0625 | 95 | 425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 2.125 | 4.4737 | 0.415 | 0.88187 | 4.75 | 21.25
[10 empty] | Total | 7.3941 | 579.75 | 2642.25
| 1290 | total customers
| 11300400 | total (customers*8760)
| 579.75 | total F
| 0.44942 | SAIFI=total F/total customers
| 2.0483 | SAIDI=total G/total customers
| 4.5576 | CAIDI=SAIDI/SAIFI
| 0.99977 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00023382 | ASUI=1-ASAI
| 7394.125 | ENS=total ENS*1000
| 5.7319 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 1.7725 | 1.3178 | 0.545 | 0.96601 | 295.9 | 389.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 1.7725 | 1.3178 | 0.545 | 0.96601 | 295.9 | 389.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 2.835 | 2.1078 | 0.545 | 1.5451 | 295.9 | 623.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 2.835 | 2.1078 | 0.545 | 1.5451 | 295.9 | 623.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 1.735 | 1.29 | 0.5 | 0.8675 | 269 | 347
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 2.835 | 2.1078 | 0.5 | 1.4175 | 269 | 567
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 2.835 | 2.1078 | 0.415 | 1.1765 | 13.45 | 28.35
[10 empty] | Total | 8.4837 | 1735.05 | 2969.65
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1735.05 | total F
| 1.345 | SAIFI=total F/total customers
| 2.3021 | SAIDI=total G/total customers
| 1.7116 | CAIDI=SAIDI/SAIFI
| 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00026279 | ASUI=1-ASAI
| 8483.7 | ENS=total ENS*1000
| 6.5765 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.315 | 3.0581 | 0.545 | 0.71668 | 94.6 | 289.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.43 |  | 1.315 | 3.0581 | 0.545 | 0.71668 | 94.6 | 289.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.415 |  | 1.27 | 3.0602 | 0.545 | 0.69215 | 91.3 | 279.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.315 | 2.7684 | 0.545 | 0.71668 | 104.5 | 289.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.27 | 2.6737 | 0.5 | 0.635 | 95 | 254
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.315 | 2.7684 | 0.5 | 0.6575 | 95 | 263
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0 | 0
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.475 |  | 1.27 | 2.6737 | 0.415 | 0.52705 | 4.75 | 12.7
[10 empty] | Total | 4.6617 | 579.75 | 1677
| 1290 | total customers
| 11300400 | total (customers*8760)
| 579.75 | total F
| 0.44942 | SAIFI=total F/total customers
| 1.3 | SAIDI=total G/total customers
| 2.8926 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001484 | ASUI=1-ASAI
| 4661.725 | ENS=total ENS*1000
| 3.6137 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 1.9131 | 1.4224 | 0.545 | 1.0427 | 295.9 | 420.8875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 62 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 3.1256 | 2.3239 | 0.545 | 1.7035 | 295.9 | 687.6375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 5.4287 | 4.0362 | 0.545 | 2.9587 | 295.9 | 1194.325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 5.4287 | 4.0362 | 0.545 | 2.9587 | 295.9 | 1194.325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 0.5 | 0.028125
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 0.5 | 0.03
|  |  | 67 | 0.6 | 0.075 | 0.045 | 0.5 | 0.0225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.345 |  | 6.6319 | 4.9308 | 0.5 | 3.3159 | 269 | 1326.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.5 | 4.4675 | 269 | 1787
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 58 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 60 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 63 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 65 | 0.75 | 0.075 | 0.05625 | 3 | 0.16875
|  |  | 57 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 59 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 61 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 62 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 64 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | 66 | 0.8 | 0.075 | 0.06 | 3 | 0.18
|  |  | 67 | 0.6 | 0.075 | 0.045 | 3 | 0.135
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.345 |  | 8.935 | 6.6431 | 0.415 | 3.708 | 13.45 | 89.35
[10 empty] | Total | 20.1549 | 1735.05 | 6699.9
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1735.05 | total F
| 1.345 | SAIFI=total F/total customers
| 5.1937 | SAIDI=total G/total customers
| 3.8615 | CAIDI=SAIDI/SAIFI
| 0.99941 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00059289 | ASUI=1-ASAI
| 20154.9188 | ENS=total ENS*1000
| 15.624 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 4563.3375 | 1100 | 31480.3125 | 1100 | 6998.4 | 1100 | 8240.1562 | 1100 | 4563.3375 | 1100 | 19498.5781 | 1100
Feeder 2 | 856.875 | 3 | 3425.625 | 3 | 2300.625 | 3 | 1044.375 | 3 | 856.875 | 3 | 2478.75 | 3
Feeder 3 | 4486.2469 | 1080 | 30920.7938 | 1080 | 7070.5688 | 1080 | 8100.0281 | 1080 | 4486.2469 | 1080 | 20086.0281 | 1080
Feeder 4 | 5208.8375 | 1300 | 40516.0375 | 1300 | 8065.9625 | 1300 | 10533.725 | 1300 | 5208.8375 | 1300 | 24965.6625 | 1300
Feeder 5 | 725.625 | 3 | 2902.5 | 3 | 1935 | 3 | 886.875 | 3 | 725.625 | 3 | 2133.75 | 3
Feeder 6 | 814.6875 | 3 | 3386.25 | 3 | 2356.875 | 3 | 986.25 | 3 | 814.6875 | 3 | 2570.625 | 3
Feeder 7 | 4661.725 | 1290 | 32121.325 | 1290 | 7394.125 | 1290 | 8483.7 | 1290 | 4661.725 | 1290 | 20154.9188 | 1290
TOTAL | 21317.3344 | 4779 | 144752.8438 | 4779 | 36121.5563 | 4779 | 38275.1094 | 4779 | 21317.3344 | 4779 | 91888.3125 | 4779
Analytic | 21.3173 |  | 144.7528 |  | 36.1216 |  | 38.2751 |  | 21.3173 |  | 91.8883
Monte Carlo_Code | 21.316 |  | 144.74 |  | 35.558 |  | 38.275 |  | 21.311 |  | 90.968
Deviation | 0.0062596 |  | 0.0088729 |  | 1.5602 |  | 0.00028576 |  | 0.029715 |  | 1.0016
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 21.316 | 21.313 | 21.319 | 21.311 |  | 945000 | 144.7 | 144.64 | 144.82 | 144.74
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 35.55 | 35.508 | 35.532 | 35.558 |  | 47500 | 38.319 | 38.284 | 38.293 | 38.275
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 21.321 | 21.311 | 21.293 | 21.324 |  | 1140000 | 90.907 | 90.968 | 90.92 | 90.859