## F1_(1-7)
[7 empty] | CASE A | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 4914.45
0.1 | 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 33783.75
0.1 |  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 8161.2
0.1 |  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 8872.125
0.1 |  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | E | 4914.45
0.1 |  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 21058.6875
0.1 |  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
0.1 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | Calculation |  |  | 0.53 |  | 1.365 | 2.5755 | 0.545 | 0.74393 | 116.6 | 300.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.545 |  | 1.41 | 2.5872 | 0.545 | 0.76845 | 119.9 | 310.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 1.365 | 2.5755 | 0.545 | 0.74393 | 116.6 | 300.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.425 | 2.28 | 0.545 | 0.77663 | 137.5 | 313.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.41 | 2.256 | 0.5 | 0.705 | 125 | 282
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.425 | 2.28 | 0.415 | 0.59137 | 6.25 | 14.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.41 | 2.256 | 0.415 | 0.58515 | 6.25 | 14.1
[10 empty] | Total | 4.9145 | 628.1 | 1534.65
| 1100 | total customers
| 9636000 | total (customers*8760)
| 628.1 | total F
| 0.571 | SAIFI=total F/total customers
| 1.3951 | SAIDI=total G/total customers
| 2.4433 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015926 | ASUI=1-ASAI
| 4914.45 | ENS=total ENS*1000
| 4.4677 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.545 | 5.2456 | 346.5 | 2117.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.545 | 5.2456 | 346.5 | 2117.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.545 | 5.2456 | 346.5 | 2117.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.545 | 5.2456 | 346.5 | 2117.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.5 | 4.8125 | 315 | 1925
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.415 | 3.9944 | 15.75 | 96.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.415 | 3.9944 | 15.75 | 96.25
[10 empty] | Total | 33.7837 | 1732.5 | 10587.5
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1732.5 | total F
| 1.575 | SAIFI=total F/total customers
| 9.625 | SAIDI=total G/total customers
| 6.1111 | CAIDI=SAIDI/SAIFI
| 0.9989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010987 | ASUI=1-ASAI
| 33783.75 | ENS=total ENS*1000
| 30.7125 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 2.29 | 4.3208 | 0.545 | 1.2481 | 116.6 | 503.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.545 |  | 2.335 | 4.2844 | 0.545 | 1.2726 | 119.9 | 513.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 2.29 | 4.3208 | 0.545 | 1.2481 | 116.6 | 503.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 2.35 | 3.76 | 0.545 | 1.2808 | 137.5 | 517
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 2.335 | 3.736 | 0.5 | 1.1675 | 125 | 467
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 2.35 | 3.76 | 0.415 | 0.97525 | 6.25 | 23.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 2.335 | 3.736 | 0.415 | 0.96902 | 6.25 | 23.35
[10 empty] | Total | 8.1612 | 628.1 | 2552.15
| 1100 | total customers
| 9636000 | total (customers*8760)
| 628.1 | total F
| 0.571 | SAIFI=total F/total customers
| 2.3201 | SAIDI=total G/total customers
| 4.0633 | CAIDI=SAIDI/SAIFI
| 0.99974 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00026486 | ASUI=1-ASAI
| 8161.2 | ENS=total ENS*1000
| 7.4193 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 1.8875 | 1.1984 | 0.545 | 1.0287 | 346.5 | 415.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 1.925 | 1.2222 | 0.545 | 1.0491 | 346.5 | 423.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 1.8875 | 1.1984 | 0.545 | 1.0287 | 346.5 | 415.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 3.075 | 1.9524 | 0.545 | 1.6759 | 346.5 | 676.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 3.075 | 1.9524 | 0.5 | 1.5375 | 315 | 615
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 3.075 | 1.9524 | 0.415 | 1.2761 | 15.75 | 30.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 3.075 | 1.9524 | 0.415 | 1.2761 | 15.75 | 30.75
[10 empty] | Total | 8.8721 | 1732.5 | 2607
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1732.5 | total F
| 1.575 | SAIFI=total F/total customers
| 2.37 | SAIDI=total G/total customers
| 1.5048 | CAIDI=SAIDI/SAIFI
| 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00027055 | ASUI=1-ASAI
| 8872.125 | ENS=total ENS*1000
| 8.0656 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 1.365 | 2.5755 | 0.545 | 0.74393 | 116.6 | 300.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.545 |  | 1.41 | 2.5872 | 0.545 | 0.76845 | 119.9 | 310.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 1.365 | 2.5755 | 0.545 | 0.74393 | 116.6 | 300.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.425 | 2.28 | 0.545 | 0.77663 | 137.5 | 313.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.41 | 2.256 | 0.5 | 0.705 | 125 | 282
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.425 | 2.28 | 0.415 | 0.59137 | 6.25 | 14.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.625 |  | 1.41 | 2.256 | 0.415 | 0.58515 | 6.25 | 14.1
[10 empty] | Total | 4.9145 | 628.1 | 1534.65
| 1100 | total customers
| 9636000 | total (customers*8760)
| 628.1 | total F
| 0.571 | SAIFI=total F/total customers
| 1.3951 | SAIDI=total G/total customers
| 2.4433 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015926 | ASUI=1-ASAI
| 4914.45 | ENS=total ENS*1000
| 4.4677 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 2.075 | 1.3175 | 0.545 | 1.1309 | 346.5 | 456.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 3.4125 | 2.1667 | 0.545 | 1.8598 | 346.5 | 750.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 9 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 4.7125 | 2.9921 | 0.545 | 2.5683 | 346.5 | 1036.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 7.1875 | 4.5635 | 0.545 | 3.9172 | 346.5 | 1581.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 12 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.575 |  | 7.1875 | 4.5635 | 0.5 | 3.5938 | 315 | 1437.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.415 | 3.9944 | 15.75 | 96.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 3 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 5 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 7 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 10 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 2 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 4 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 6 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 8 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 9 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 11 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 12 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.575 |  | 9.625 | 6.1111 | 0.415 | 3.9944 | 15.75 | 96.25
[10 empty] | Total | 21.0587 | 1732.5 | 5455.25
| 1100 | total customers
| 9636000 | total (customers*8760)
| 1732.5 | total F
| 1.575 | SAIFI=total F/total customers
| 4.9593 | SAIDI=total G/total customers
| 3.1488 | CAIDI=SAIDI/SAIFI
| 0.99943 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00056613 | ASUI=1-ASAI
| 21058.6875 | ENS=total ENS*1000
| 19.1443 | AENS=ENS/total customers

## F2_(8-10)
[7 empty] | CASE A & E | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1142.5
0.1 | 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | B | 4567.5
0.1 |  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 3067.5
0.1 |  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | D | 1392.5
0.1 |  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18 | [5 empty] | E | 1142.5
0.1 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 3305
0.1 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | Calculation |  |  | 0.28 |  | 0.29 | 1.0357 | 1 | 0.29 | 0.28 | 0.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.335 | 1.1356 | 1.5 | 0.5025 | 0.295 | 0.335
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.3 |  | 0.35 | 1.1667 | 1 | 0.35 | 0.3 | 0.35
[10 empty] | Total | 1.1425 | 0.875 | 0.975
| 3 | total customers
| 26280 | total (customers*8760)
| 0.875 | total F
| 0.29167 | SAIFI=total F/total customers
| 0.325 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.71e-05 | ASUI=1-ASAI
| 1142.5 | ENS=total ENS*1000
| 380.8333 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1 | 1.305 | 0.435 | 1.305
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1.5 | 1.9575 | 0.435 | 1.305
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1 | 1.305 | 0.435 | 1.305
[10 empty] | Total | 4.5675 | 1.305 | 3.915
| 3 | total customers
| 26280 | total (customers*8760)
| 1.305 | total F
| 0.435 | SAIFI=total F/total customers
| 1.305 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014897 | ASUI=1-ASAI
| 4567.5 | ENS=total ENS*1000
| 1522.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.28 |  | 0.84 | 3 | 1 | 0.84 | 0.28 | 0.84
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.885 | 3 | 1.5 | 1.3275 | 0.295 | 0.885
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.3 |  | 0.9 | 3 | 1 | 0.9 | 0.3 | 0.9
[10 empty] | Total | 3.0675 | 0.875 | 2.625
| 3 | total customers
| 26280 | total (customers*8760)
| 0.875 | total F
| 0.29167 | SAIFI=total F/total customers
| 0.875 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 9.9886e-05 | ASUI=1-ASAI
| 3067.5 | ENS=total ENS*1000
| 1022.5 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 18 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | Calculation |  |  | 0.435 |  | 0.3675 | 0.84483 | 1 | 0.3675 | 0.435 | 0.3675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | Calculation |  |  | 0.435 |  | 0.405 | 0.93103 | 1.5 | 0.6075 | 0.435 | 0.405
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 16 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 0.4175 | 0.95977 | 1 | 0.4175 | 0.435 | 0.4175
[10 empty] | Total | 1.3925 | 1.305 | 1.19
| 3 | total customers
| 26280 | total (customers*8760)
| 1.305 | total F
| 0.435 | SAIFI=total F/total customers
| 0.39667 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.5282e-05 | ASUI=1-ASAI
| 1392.5 | ENS=total ENS*1000
| 464.1667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 18 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | Calculation |  |  | 0.435 |  | 0.5675 | 1.3046 | 1 | 0.5675 | 0.435 | 0.5675
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | Calculation |  |  | 0.435 |  | 0.955 | 2.1954 | 1.5 | 1.4325 | 0.435 | 0.955
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 15 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 17 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 14 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 16 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 18 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1 | 1.305 | 0.435 | 1.305
[10 empty] | Total | 3.305 | 1.305 | 2.8275
| 3 | total customers
| 26280 | total (customers*8760)
| 1.305 | total F
| 0.435 | SAIFI=total F/total customers
| 0.9425 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00010759 | ASUI=1-ASAI
| 3305 | ENS=total ENS*1000
| 1101.6667 | AENS=ENS/total customers

## F3_(11-17)
[7 empty] | CASE A | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 4826.6625
0.1 | 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 33142.725
0.1 |  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 8272.425
0.1 |  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 8704.7875
0.1 |  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | E | 4826.6625
0.1 |  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 21587.5375
0.1 |  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
0.1 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | Calculation |  |  | 0.535 |  | 1.4175 | 2.6495 | 0.545 | 0.77254 | 117.7 | 311.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 1.4025 | 2.6462 | 0.545 | 0.76436 | 116.6 | 308.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 1.4025 | 2.6462 | 0.545 | 0.76436 | 116.6 | 308.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.3575 | 2.3008 | 0.5 | 0.67875 | 118 | 271.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.4025 | 2.3771 | 0.5 | 0.70125 | 118 | 280.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.4025 | 2.3771 | 0.415 | 0.58204 | 5.9 | 14.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.3575 | 2.3008 | 0.415 | 0.56336 | 5.9 | 13.575
[10 empty] | Total | 4.8267 | 598.7 | 1508.55
| 1080 | total customers
| 9460800 | total (customers*8760)
| 598.7 | total F
| 0.55435 | SAIFI=total F/total customers
| 1.3968 | SAIDI=total G/total customers
| 2.5197 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015945 | ASUI=1-ASAI
| 4826.6625 | ENS=total ENS*1000
| 4.4691 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.545 | 5.2129 | 342.1 | 2104.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.545 | 5.2129 | 342.1 | 2104.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.545 | 5.2129 | 342.1 | 2104.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.5 | 4.7825 | 311 | 1913
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.5 | 4.7825 | 311 | 1913
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.415 | 3.9695 | 15.55 | 95.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.415 | 3.9695 | 15.55 | 95.65
[10 empty] | Total | 33.1427 | 1679.4 | 10330.2
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1679.4 | total F
| 1.555 | SAIFI=total F/total customers
| 9.565 | SAIDI=total G/total customers
| 6.1511 | CAIDI=SAIDI/SAIFI
| 0.99891 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010919 | ASUI=1-ASAI
| 33142.725 | ENS=total ENS*1000
| 30.6877 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.535 |  | 2.305 | 4.3084 | 0.545 | 1.2562 | 117.7 | 507.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 2.29 | 4.3208 | 0.545 | 1.2481 | 116.6 | 503.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 2.29 | 4.3208 | 0.545 | 1.2481 | 116.6 | 503.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 2.47 | 4.1864 | 0.5 | 1.235 | 118 | 494
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 2.47 | 4.1864 | 0.5 | 1.235 | 118 | 494
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 2.47 | 4.1864 | 0.415 | 1.025 | 5.9 | 24.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 2.47 | 4.1864 | 0.415 | 1.025 | 5.9 | 24.7
[10 empty] | Total | 8.2724 | 598.7 | 2552.1
| 1080 | total customers
| 9460800 | total (customers*8760)
| 598.7 | total F
| 0.55435 | SAIFI=total F/total customers
| 2.3631 | SAIDI=total G/total customers
| 4.2627 | CAIDI=SAIDI/SAIFI
| 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00026976 | ASUI=1-ASAI
| 8272.425 | ENS=total ENS*1000
| 7.6597 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 1.9275 | 1.2395 | 0.545 | 1.0505 | 342.1 | 424.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 1.915 | 1.2315 | 0.545 | 1.0437 | 342.1 | 421.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 3.015 | 1.9389 | 0.545 | 1.6432 | 342.1 | 663.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 3.015 | 1.9389 | 0.5 | 1.5075 | 311 | 603
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 1.915 | 1.2315 | 0.5 | 0.9575 | 311 | 383
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 3.015 | 1.9389 | 0.415 | 1.2512 | 15.55 | 30.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 3.015 | 1.9389 | 0.415 | 1.2512 | 15.55 | 30.15
[10 empty] | Total | 8.7048 | 1679.4 | 2554.95
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1679.4 | total F
| 1.555 | SAIFI=total F/total customers
| 2.3657 | SAIDI=total G/total customers
| 1.5213 | CAIDI=SAIDI/SAIFI
| 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00027006 | ASUI=1-ASAI
| 8704.7875 | ENS=total ENS*1000
| 8.06 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.535 |  | 1.4175 | 2.6495 | 0.545 | 0.77254 | 117.7 | 311.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 1.4025 | 2.6462 | 0.545 | 0.76436 | 116.6 | 308.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.53 |  | 1.4025 | 2.6462 | 0.545 | 0.76436 | 116.6 | 308.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.3575 | 2.3008 | 0.5 | 0.67875 | 118 | 271.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.4025 | 2.3771 | 0.5 | 0.70125 | 118 | 280.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.4025 | 2.3771 | 0.415 | 0.58204 | 5.9 | 14.025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0 | 0
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.59 |  | 1.3575 | 2.3008 | 0.415 | 0.56336 | 5.9 | 13.575
[10 empty] | Total | 4.8267 | 598.7 | 1508.55
| 1080 | total customers
| 9460800 | total (customers*8760)
| 598.7 | total F
| 0.55435 | SAIFI=total F/total customers
| 1.3968 | SAIDI=total G/total customers
| 2.5197 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015945 | ASUI=1-ASAI
| 4826.6625 | ENS=total ENS*1000
| 4.4691 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 2.115 | 1.3601 | 0.545 | 1.1527 | 342.1 | 465.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 25 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 3.4025 | 2.1881 | 0.545 | 1.8544 | 342.1 | 748.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 5.84 | 3.7556 | 0.545 | 3.1828 | 342.1 | 1284.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.555 |  | 5.84 | 3.7556 | 0.5 | 2.92 | 311 | 1168
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 30 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.0775 | 5.8376 | 0.5 | 4.5388 | 311 | 1815.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.415 | 3.9695 | 15.55 | 95.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 21 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 23 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 26 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 28 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 20 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 22 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 24 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 25 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 27 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 29 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 30 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.555 |  | 9.565 | 6.1511 | 0.415 | 3.9695 | 15.55 | 95.65
[10 empty] | Total | 21.5875 | 1679.4 | 5673.45
| 1080 | total customers
| 9460800 | total (customers*8760)
| 1679.4 | total F
| 1.555 | SAIFI=total F/total customers
| 5.2532 | SAIDI=total G/total customers
| 3.3783 | CAIDI=SAIDI/SAIFI
| 0.9994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00059968 | ASUI=1-ASAI
| 21587.5375 | ENS=total ENS*1000
| 19.9885 | AENS=ENS/total customers

## F4_(18-25)
[7 empty] | CASE A | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 5608.45
0.1 | 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | B | 43328.05
0.1 |  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 9417.95
0.1 |  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 11301.55
0.1 |  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | E | 5608.45
0.1 |  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | F | 26837.55
0.1 |  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
0.1 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.1 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.545 | 0.74665 | 118.8 | 301.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.5 | 0.685 | 108 | 274
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.5 | 0.7075 | 111 | 283
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.415 | 0.58722 | 5.55 | 14.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.415 | 0.56855 | 5.4 | 13.7
[10 empty] | Total | 5.6085 | 715.05 | 1820.15
| 1300 | total customers
| 11388000 | total (customers*8760)
| 715.05 | total F
| 0.55004 | SAIFI=total F/total customers
| 1.4001 | SAIDI=total G/total customers
| 2.5455 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015983 | ASUI=1-ASAI
| 5608.45 | ENS=total ENS*1000
| 4.3142 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.545 | 5.8887 | 381.7 | 2377.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.545 | 5.8887 | 381.7 | 2377.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.545 | 5.8887 | 381.7 | 2377.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.545 | 5.8887 | 381.7 | 2377.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.5 | 5.4025 | 347 | 2161
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.5 | 5.4025 | 347 | 2161
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.415 | 4.4841 | 17.35 | 108.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.415 | 4.4841 | 17.35 | 108.05
[10 empty] | Total | 43.328 | 2255.5 | 14046.5
| 1300 | total customers
| 11388000 | total (customers*8760)
| 2255.5 | total F
| 1.735 | SAIFI=total F/total customers
| 10.805 | SAIDI=total G/total customers
| 6.2277 | CAIDI=SAIDI/SAIFI
| 0.99877 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012334 | ASUI=1-ASAI
| 43328.05 | ENS=total ENS*1000
| 33.3293 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.545 | 1.2889 | 122.1 | 520.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.545 | 1.2644 | 118.8 | 510.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.545 | 1.2889 | 122.1 | 520.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.545 | 1.2889 | 122.1 | 520.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.5 | 1.16 | 108 | 464
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.5 | 1.1825 | 111 | 473
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 2.365 | 4.2613 | 0.415 | 0.98147 | 5.55 | 23.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.415 | 0.9628 | 5.4 | 23.2
[10 empty] | Total | 9.418 | 715.05 | 3055.15
| 1300 | total customers
| 11388000 | total (customers*8760)
| 715.05 | total F
| 0.55004 | SAIFI=total F/total customers
| 2.3501 | SAIDI=total G/total customers
| 4.2726 | CAIDI=SAIDI/SAIFI
| 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00026828 | ASUI=1-ASAI
| 9417.95 | ENS=total ENS*1000
| 7.2446 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 2.005 | 1.1556 | 0.545 | 1.0927 | 381.7 | 441.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.545 | 1.6922 | 381.7 | 683.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.545 | 1.6922 | 381.7 | 683.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.545 | 1.6922 | 381.7 | 683.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.5 | 1.5525 | 347 | 621
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 2.005 | 1.1556 | 0.5 | 1.0025 | 347 | 401
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.415 | 1.2886 | 17.35 | 31.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 3.105 | 1.7896 | 0.415 | 1.2886 | 17.35 | 31.05
[10 empty] | Total | 11.3015 | 2255.5 | 3574.5
| 1300 | total customers
| 11388000 | total (customers*8760)
| 2255.5 | total F
| 1.735 | SAIFI=total F/total customers
| 2.7496 | SAIDI=total G/total customers
| 1.5848 | CAIDI=SAIDI/SAIFI
| 0.99969 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00031388 | ASUI=1-ASAI
| 11301.55 | ENS=total ENS*1000
| 8.6935 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.545 | 0.74665 | 118.8 | 301.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.545 | 0.77118 | 122.1 | 311.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.5 | 0.685 | 108 | 274
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.5 | 0.7075 | 111 | 283
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.555 |  | 1.415 | 2.5495 | 0.415 | 0.58722 | 5.55 | 14.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.37 | 2.537 | 0.415 | 0.56855 | 5.4 | 13.7
[10 empty] | Total | 5.6085 | 715.05 | 1820.15
| 1300 | total customers
| 11388000 | total (customers*8760)
| 715.05 | total F
| 0.55004 | SAIFI=total F/total customers
| 1.4001 | SAIDI=total G/total customers
| 2.5455 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015983 | ASUI=1-ASAI
| 5608.45 | ENS=total ENS*1000
| 4.3142 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 35 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 2.205 | 1.2709 | 0.545 | 1.2017 | 381.7 | 485.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 4.6425 | 2.6758 | 0.545 | 2.5302 | 381.7 | 1021.35
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 38 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 4.6425 | 2.6758 | 0.545 | 2.5302 | 381.7 | 1021.35
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 7.08 | 4.0807 | 0.545 | 3.8586 | 381.7 | 1557.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 7.08 | 4.0807 | 0.5 | 3.54 | 347 | 1416
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 43 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.735 |  | 8.4175 | 4.8516 | 0.5 | 4.2088 | 347 | 1683.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.415 | 4.4841 | 17.35 | 108.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 33 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 36 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 39 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 41 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 32 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 34 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 35 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 37 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 38 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 40 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 42 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 43 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.735 |  | 10.805 | 6.2277 | 0.415 | 4.4841 | 17.35 | 108.05
[10 empty] | Total | 26.8376 | 2255.5 | 7401
| 1300 | total customers
| 11388000 | total (customers*8760)
| 2255.5 | total F
| 1.735 | SAIFI=total F/total customers
| 5.6931 | SAIDI=total G/total customers
| 3.2813 | CAIDI=SAIDI/SAIFI
| 0.99935 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00064989 | ASUI=1-ASAI
| 26837.55 | ENS=total ENS*1000
| 20.6443 | AENS=ENS/total customers

## F5_(26-28)
[7 empty] | CASE A & E | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 967.5
0.1 | 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | B | 3870
0.1 |  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 2580
0.1 |  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | D | 1182.5
0.1 |  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225 | [5 empty] | E | 967.5
0.1 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 2845
0.1 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | Calculation |  |  | 0.29 |  | 0.3325 | 1.1466 | 1 | 0.3325 | 0.29 | 0.3325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.3475 | 1.178 | 1 | 0.3475 | 0.295 | 0.3475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.275 |  | 0.2875 | 1.0455 | 1 | 0.2875 | 0.275 | 0.2875
[10 empty] | Total | 0.9675 | 0.86 | 0.9675
| 3 | total customers
| 26280 | total (customers*8760)
| 0.86 | total F
| 0.28667 | SAIFI=total F/total customers
| 0.3225 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.6815e-05 | ASUI=1-ASAI
| 967.5 | ENS=total ENS*1000
| 322.5 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
[10 empty] | Total | 3.87 | 1.29 | 3.87
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 1.29 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014726 | ASUI=1-ASAI
| 3870 | ENS=total ENS*1000
| 1290 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.29 |  | 0.87 | 3 | 1 | 0.87 | 0.29 | 0.87
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.885 | 3 | 1 | 0.885 | 0.295 | 0.885
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.275 |  | 0.825 | 3 | 1 | 0.825 | 0.275 | 0.825
[10 empty] | Total | 2.58 | 0.86 | 2.58
| 3 | total customers
| 26280 | total (customers*8760)
| 0.86 | total F
| 0.28667 | SAIFI=total F/total customers
| 0.86 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 9.8174e-05 | ASUI=1-ASAI
| 2580 | ENS=total ENS*1000
| 860 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 49 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.4025 | 0.93605 | 1 | 0.4025 | 0.43 | 0.4025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.415 | 0.96512 | 1 | 0.415 | 0.43 | 0.415
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 47 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 0.365 | 0.84884 | 1 | 0.365 | 0.43 | 0.365
[10 empty] | Total | 1.1825 | 1.29 | 1.1825
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.39417 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.4996e-05 | ASUI=1-ASAI
| 1182.5 | ENS=total ENS*1000
| 394.1667 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 49 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.6025 | 1.4012 | 1 | 0.6025 | 0.43 | 0.6025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.9525 | 2.2151 | 1 | 0.9525 | 0.43 | 0.9525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 46 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 48 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 45 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 47 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 49 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
[10 empty] | Total | 2.845 | 1.29 | 2.845
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.94833 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00010826 | ASUI=1-ASAI
| 2845 | ENS=total ENS*1000
| 948.3333 | AENS=ENS/total customers

## F6_(29-31)
[7 empty] | CASE A & E | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1086.25
0.1 | 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 4515
0.1 |  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | C | 3142.5
0.1 |  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04 | [5 empty] | D | 1315
0.1 |  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18 | [5 empty] | E | 1086.25
0.1 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 3427.5
0.1 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | Calculation |  |  | 0.295 |  | 0.2975 | 1.0085 | 1 | 0.2975 | 0.295 | 0.2975
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.31 |  | 0.3425 | 1.1048 | 1 | 0.3425 | 0.31 | 0.3425
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.295 |  | 0.2975 | 1.0085 | 1.5 | 0.44625 | 0.295 | 0.2975
[10 empty] | Total | 1.0862 | 0.9 | 0.9375
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9 | total F
| 0.3 | SAIFI=total F/total customers
| 0.3125 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 3.5674e-05 | ASUI=1-ASAI
| 1086.25 | ENS=total ENS*1000
| 362.0833 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1 | 1.29 | 0.43 | 1.29
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1.5 | 1.935 | 0.43 | 1.29
[10 empty] | Total | 4.515 | 1.29 | 3.87
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 1.29 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014726 | ASUI=1-ASAI
| 4515 | ENS=total ENS*1000
| 1505 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.295 |  | 0.885 | 3 | 1 | 0.885 | 0.295 | 0.885
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.31 |  | 0.93 | 3 | 1 | 0.93 | 0.31 | 0.93
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.295 |  | 0.885 | 3 | 1.5 | 1.3275 | 0.295 | 0.885
[10 empty] | Total | 3.1425 | 0.9 | 2.7
| 3 | total customers
| 26280 | total (customers*8760)
| 0.9 | total F
| 0.3 | SAIFI=total F/total customers
| 0.9 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.9999 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00010274 | ASUI=1-ASAI
| 3142.5 | ENS=total ENS*1000
| 1047.5 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 55 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.365 | 0.84884 | 1 | 0.365 | 0.43 | 0.365
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.4025 | 0.93605 | 1 | 0.4025 | 0.43 | 0.4025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 53 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 0.365 | 0.84884 | 1.5 | 0.5475 | 0.43 | 0.365
[10 empty] | Total | 1.315 | 1.29 | 1.1325
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.3775 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 4.3094e-05 | ASUI=1-ASAI
| 1315 | ENS=total ENS*1000
| 438.3333 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 55 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.5525 | 1.2849 | 1 | 0.5525 | 0.43 | 0.5525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | Calculation |  |  | 0.43 |  | 0.94 | 2.186 | 1 | 0.94 | 0.43 | 0.94
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 52 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 54 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 51 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 53 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 55 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | Calculation |  |  | 0.43 |  | 1.29 | 3 | 1.5 | 1.935 | 0.43 | 1.29
[10 empty] | Total | 3.4275 | 1.29 | 2.7825
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.9275 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99989 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00010588 | ASUI=1-ASAI
| 3427.5 | ENS=total ENS*1000
| 1142.5 | AENS=ENS/total customers

## F7_(32-38)
[7 empty] | CASE A | [6 empty] | ENS
0.1 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 5017.3
0.1 | 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | B | 34440.1
0.1 |  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03 | [5 empty] | C | 8660.5
0.1 |  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | D | 9118.85
0.1 |  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | E | 5017.3
0.1 |  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375 | [5 empty] | F | 21735.475
0.1 |  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
0.1 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.1 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.1 |  |  | x former |  |  | 0.1 | 10 | 1
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | x former |  |  | 0 | 0 | 0
0.1 |  |  | Calculation |  |  | 0.54 |  | 1.42 | 2.6296 | 0.545 | 0.7739 | 118.8 | 312.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.42 | 2.6296 | 0.545 | 0.7739 | 118.8 | 312.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.52 |  | 1.36 | 2.6154 | 0.545 | 0.7412 | 114.4 | 299.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.42 | 2.3667 | 0.545 | 0.7739 | 132 | 312.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.36 | 2.2667 | 0.5 | 0.68 | 120 | 272
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.42 | 2.3667 | 0.5 | 0.71 | 120 | 284
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.36 | 2.2667 | 0.415 | 0.5644 | 6 | 13.6
[10 empty] | Total | 5.0173 | 730 | 1806
| 1290 | total customers
| 11300400 | total (customers*8760)
| 730 | total F
| 0.56589 | SAIFI=total F/total customers
| 1.4 | SAIDI=total G/total customers
| 2.474 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015982 | ASUI=1-ASAI
| 5017.3 | ENS=total ENS*1000
| 3.8894 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.545 | 5.2211 | 343.2 | 2107.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.545 | 5.2211 | 343.2 | 2107.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.545 | 5.2211 | 343.2 | 2107.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.545 | 5.2211 | 343.2 | 2107.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.5 | 4.79 | 312 | 1916
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.5 | 4.79 | 312 | 1916
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.415 | 3.9757 | 15.6 | 95.8
[10 empty] | Total | 34.4401 | 2012.4 | 12358.2
| 1290 | total customers
| 11300400 | total (customers*8760)
| 2012.4 | total F
| 1.56 | SAIFI=total F/total customers
| 9.58 | SAIDI=total G/total customers
| 6.141 | CAIDI=SAIDI/SAIFI
| 0.99891 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0010936 | ASUI=1-ASAI
| 34440.1 | ENS=total ENS*1000
| 26.6978 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.545 | 1.2644 | 118.8 | 510.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 2.32 | 4.2963 | 0.545 | 1.2644 | 118.8 | 510.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.52 |  | 2.26 | 4.3462 | 0.545 | 1.2317 | 114.4 | 497.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 2.5 | 4.1667 | 0.545 | 1.3625 | 132 | 550
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 2.5 | 4.1667 | 0.5 | 1.25 | 120 | 500
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 2.5 | 4.1667 | 0.5 | 1.25 | 120 | 500
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 2.5 | 4.1667 | 0.415 | 1.0375 | 6 | 25
[10 empty] | Total | 8.6605 | 730 | 3093
| 1290 | total customers
| 11300400 | total (customers*8760)
| 730 | total F
| 0.56589 | SAIFI=total F/total customers
| 2.3977 | SAIDI=total G/total customers
| 4.237 | CAIDI=SAIDI/SAIFI
| 0.99973 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00027371 | ASUI=1-ASAI
| 8660.5 | ENS=total ENS*1000
| 6.7136 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 1.93 | 1.2372 | 0.545 | 1.0519 | 343.2 | 424.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 1.93 | 1.2372 | 0.545 | 1.0519 | 343.2 | 424.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 3.03 | 1.9423 | 0.545 | 1.6513 | 343.2 | 666.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 3.03 | 1.9423 | 0.545 | 1.6513 | 343.2 | 666.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 1.88 | 1.2051 | 0.5 | 0.94 | 312 | 376
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 3.03 | 1.9423 | 0.5 | 1.515 | 312 | 606
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 3.03 | 1.9423 | 0.415 | 1.2574 | 15.6 | 30.3
[10 empty] | Total | 9.1189 | 2012.4 | 3194.7
| 1290 | total customers
| 11300400 | total (customers*8760)
| 2012.4 | total F
| 1.56 | SAIFI=total F/total customers
| 2.4765 | SAIDI=total G/total customers
| 1.5875 | CAIDI=SAIDI/SAIFI
| 0.99972 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00028271 | ASUI=1-ASAI
| 9118.85 | ENS=total ENS*1000
| 7.0689 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.42 | 2.6296 | 0.545 | 0.7739 | 118.8 | 312.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.54 |  | 1.42 | 2.6296 | 0.545 | 0.7739 | 118.8 | 312.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.52 |  | 1.36 | 2.6154 | 0.545 | 0.7412 | 114.4 | 299.2
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.42 | 2.3667 | 0.545 | 0.7739 | 132 | 312.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.36 | 2.2667 | 0.5 | 0.68 | 120 | 272
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.42 | 2.3667 | 0.5 | 0.71 | 120 | 284
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0 | 0
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.6 |  | 1.36 | 2.2667 | 0.415 | 0.5644 | 6 | 13.6
[10 empty] | Total | 5.0173 | 730 | 1806
| 1290 | total customers
| 11300400 | total (customers*8760)
| 730 | total F
| 0.56589 | SAIFI=total F/total customers
| 1.4 | SAIDI=total G/total customers
| 2.474 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015982 | ASUI=1-ASAI
| 5017.3 | ENS=total ENS*1000
| 3.8894 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 2.1175 | 1.3574 | 0.545 | 1.154 | 343.2 | 465.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 62 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 3.4175 | 2.1907 | 0.545 | 1.8625 | 343.2 | 751.85
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 5.855 | 3.7532 | 0.545 | 3.191 | 343.2 | 1288.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 5.855 | 3.7532 | 0.545 | 3.191 | 343.2 | 1288.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 0.5 | 0.0375
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 0.5 | 0.04
|  |  | 67 | 0.6 | 0.1 | 0.06 | 0.5 | 0.03
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.56 |  | 7.1425 | 4.5785 | 0.5 | 3.5713 | 312 | 1428.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.5 | 4.79 | 312 | 1916
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 58 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 60 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 63 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 65 | 0.75 | 0.1 | 0.075 | 3 | 0.225
|  |  | 57 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 59 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 61 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 62 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 64 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | 66 | 0.8 | 0.1 | 0.08 | 3 | 0.24
|  |  | 67 | 0.6 | 0.1 | 0.06 | 3 | 0.18
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.56 |  | 9.58 | 6.141 | 0.415 | 3.9757 | 15.6 | 95.8
[10 empty] | Total | 21.7355 | 2012.4 | 7234.2
| 1290 | total customers
| 11300400 | total (customers*8760)
| 2012.4 | total F
| 1.56 | SAIFI=total F/total customers
| 5.6079 | SAIDI=total G/total customers
| 3.5948 | CAIDI=SAIDI/SAIFI
| 0.99936 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00064017 | ASUI=1-ASAI
| 21735.475 | ENS=total ENS*1000
| 16.8492 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 4914.45 | 1100 | 33783.75 | 1100 | 8161.2 | 1100 | 8872.125 | 1100 | 4914.45 | 1100 | 21058.6875 | 1100
Feeder 2 | 1142.5 | 3 | 4567.5 | 3 | 3067.5 | 3 | 1392.5 | 3 | 1142.5 | 3 | 3305 | 3
Feeder 3 | 4826.6625 | 1080 | 33142.725 | 1080 | 8272.425 | 1080 | 8704.7875 | 1080 | 4826.6625 | 1080 | 21587.5375 | 1080
Feeder 4 | 5608.45 | 1300 | 43328.05 | 1300 | 9417.95 | 1300 | 11301.55 | 1300 | 5608.45 | 1300 | 26837.55 | 1300
Feeder 5 | 967.5 | 3 | 3870 | 3 | 2580 | 3 | 1182.5 | 3 | 967.5 | 3 | 2845 | 3
Feeder 6 | 1086.25 | 3 | 4515 | 3 | 3142.5 | 3 | 1315 | 3 | 1086.25 | 3 | 3427.5 | 3
Feeder 7 | 5017.3 | 1290 | 34440.1 | 1290 | 8660.5 | 1290 | 9118.85 | 1290 | 5017.3 | 1290 | 21753.48 | 1290
TOTAL | 23563.1125 | 4779 | 157647.125 | 4779 | 43302.075 | 4779 | 41887.3125 | 4779 | 23563.1125 | 4779 | 100814.755 | 4779
Analytic | 23.5631 |  | 157.6471 |  | 43.3021 |  | 41.8873 |  | 23.5631 |  | 100.8148
Monte Carlo_Code | 23.558 |  | 157.58 |  | 42.515 |  | 41.885 |  | 23.561 |  | 100.01
Deviation | 0.021697 |  | 0.042579 |  | 1.8176 |  | 0.0055208 |  | 0.0089653 |  | 0.79825
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 23.576 | 23.558 | 23.644 | 23.566 |  | 945000 | 157.74 | 157.56 | 157.58 | 157.69
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 42.507 | 42.514 | 42.49 | 42.515 |  | 47500 | 41.885 | 41.892 | 41.841 | 41.882
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 23.605 | 23.557 | 23.547 | 23.561 |  | 1140000 | 100.01 | 99.834 | 99.846 | 99.914