## F1_(1-7)
[7 empty] | CASE A | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 5616.675
0.15 | 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 38390.625
0.15 |  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 10486.8
0.15 |  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 10136.0625
0.15 |  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | E | 5616.675
0.15 |  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 24178.9062
0.15 |  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
0.15 |  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | Calculation |  |  | 0.745 |  | 1.5475 | 2.0772 | 0.545 | 0.84339 | 163.9 | 340.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7675 |  | 1.615 | 2.1042 | 0.545 | 0.88018 | 168.85 | 355.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 1.5475 | 2.0772 | 0.545 | 0.84339 | 163.9 | 340.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.6375 | 1.8451 | 0.545 | 0.89244 | 195.25 | 360.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.615 | 1.8197 | 0.5 | 0.8075 | 177.5 | 323
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.6375 | 1.8451 | 0.415 | 0.67956 | 8.875 | 16.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.615 | 1.8197 | 0.415 | 0.67022 | 8.875 | 16.15
[10 empty] | Total | 5.6167 | 887.15 | 1751.975
| 1100 | total customers
| 9636000 | total (customers*8760)
| 887.15 | total F
| 0.8065 | SAIFI=total F/total customers
| 1.5927 | SAIDI=total G/total customers
| 1.9748 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018182 | ASUI=1-ASAI
| 5616.675 | ENS=total ENS*1000
| 5.1061 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.545 | 5.9609 | 442.75 | 2406.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.545 | 5.9609 | 442.75 | 2406.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.545 | 5.9609 | 442.75 | 2406.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.545 | 5.9609 | 442.75 | 2406.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.5 | 5.4688 | 402.5 | 2187.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.415 | 4.5391 | 20.125 | 109.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.415 | 4.5391 | 20.125 | 109.375
[10 empty] | Total | 38.3906 | 2213.75 | 12031.25
| 1100 | total customers
| 9636000 | total (customers*8760)
| 2213.75 | total F
| 2.0125 | SAIFI=total F/total customers
| 10.9375 | SAIDI=total G/total customers
| 5.4348 | CAIDI=SAIDI/SAIFI
| 0.99875 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012486 | ASUI=1-ASAI
| 38390.625 | ENS=total ENS*1000
| 34.9006 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 2.935 | 3.9396 | 0.545 | 1.5996 | 163.9 | 645.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0 | 0 | 3 | 0
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7675 |  | 3.0025 | 3.9121 | 0.545 | 1.6364 | 168.85 | 660.55
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 2.935 | 3.9396 | 0.545 | 1.5996 | 163.9 | 645.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 3.025 | 3.4085 | 0.545 | 1.6486 | 195.25 | 665.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 3.0025 | 3.3831 | 0.5 | 1.5012 | 177.5 | 600.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 3.025 | 3.4085 | 0.415 | 1.2554 | 8.875 | 30.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 3.0025 | 3.3831 | 0.415 | 1.246 | 8.875 | 30.025
[10 empty] | Total | 10.4868 | 887.15 | 3278.225
| 1100 | total customers
| 9636000 | total (customers*8760)
| 887.15 | total F
| 0.8065 | SAIFI=total F/total customers
| 2.9802 | SAIDI=total G/total customers
| 3.6952 | CAIDI=SAIDI/SAIFI
| 0.99966 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00034021 | ASUI=1-ASAI
| 10486.8 | ENS=total ENS*1000
| 9.5335 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 2.1812 | 1.0839 | 0.545 | 1.1888 | 442.75 | 479.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 2.2375 | 1.1118 | 0.545 | 1.2194 | 442.75 | 492.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 2.1812 | 1.0839 | 0.545 | 1.1888 | 442.75 | 479.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 3.4875 | 1.7329 | 0.545 | 1.9007 | 442.75 | 767.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 3.4875 | 1.7329 | 0.5 | 1.7437 | 402.5 | 697.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 3.4875 | 1.7329 | 0.415 | 1.4473 | 20.125 | 34.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 3.4875 | 1.7329 | 0.415 | 1.4473 | 20.125 | 34.875
[10 empty] | Total | 10.1361 | 2213.75 | 2986.5
| 1100 | total customers
| 9636000 | total (customers*8760)
| 2213.75 | total F
| 2.0125 | SAIFI=total F/total customers
| 2.715 | SAIDI=total G/total customers
| 1.3491 | CAIDI=SAIDI/SAIFI
| 0.99969 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00030993 | ASUI=1-ASAI
| 10136.0625 | ENS=total ENS*1000
| 9.2146 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 1.5475 | 2.0772 | 0.545 | 0.84339 | 163.9 | 340.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7675 |  | 1.615 | 2.1042 | 0.545 | 0.88018 | 168.85 | 355.3
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 1.5475 | 2.0772 | 0.545 | 0.84339 | 163.9 | 340.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.6375 | 1.8451 | 0.545 | 0.89244 | 195.25 | 360.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 12 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.615 | 1.8197 | 0.5 | 0.8075 | 177.5 | 323
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.6375 | 1.8451 | 0.415 | 0.67956 | 8.875 | 16.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 4 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 6 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 8 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 9 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.8875 |  | 1.615 | 1.8197 | 0.415 | 0.67022 | 8.875 | 16.15
[10 empty] | Total | 5.6167 | 887.15 | 1751.975
| 1100 | total customers
| 9636000 | total (customers*8760)
| 887.15 | total F
| 0.8065 | SAIFI=total F/total customers
| 1.5927 | SAIDI=total G/total customers
| 1.9748 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018182 | ASUI=1-ASAI
| 5616.675 | ENS=total ENS*1000
| 5.1061 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 1 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 2.4625 | 1.2236 | 0.545 | 1.3421 | 442.75 | 541.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 2 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 3.9937 | 1.9845 | 0.545 | 2.1766 | 442.75 | 878.625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 3 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 5.4687 | 2.7174 | 0.545 | 2.9805 | 442.75 | 1203.125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 4 | 220 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 8.2313 | 4.0901 | 0.545 | 4.486 | 442.75 | 1810.875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 5 | 200 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.0125 |  | 8.2313 | 4.0901 | 0.5 | 4.1156 | 402.5 | 1646.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 6 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.415 | 4.5391 | 20.125 | 109.375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 7 | 10 | 1 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 3 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 5 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 7 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 10 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 2 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 4 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 6 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 8 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 9 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 11 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 12 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.0125 |  | 10.9375 | 5.4348 | 0.415 | 4.5391 | 20.125 | 109.375
[10 empty] | Total | 24.1789 | 2213.75 | 6299.375
| 1100 | total customers
| 9636000 | total (customers*8760)
| 2213.75 | total F
| 2.0125 | SAIFI=total F/total customers
| 5.7267 | SAIDI=total G/total customers
| 2.8456 | CAIDI=SAIDI/SAIFI
| 0.99935 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00065373 | ASUI=1-ASAI
| 24178.9062 | ENS=total ENS*1000
| 21.9808 | AENS=ENS/total customers

## F2_(8-10)
[7 empty] | CASE A & E | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1713.75
0.15 | 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 6851.25
0.15 |  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 4601.25
0.15 |  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | D | 2088.75
0.15 |  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27 | [5 empty] | E | 1713.75
0.15 |  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4957.5
0.15 |  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | Calculation |  |  | 0.42 |  | 0.435 | 1.0357 | 1 | 0.435 | 0.42 | 0.435
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 0.5025 | 1.1356 | 1.5 | 0.75375 | 0.4425 | 0.5025
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.45 |  | 0.525 | 1.1667 | 1 | 0.525 | 0.45 | 0.525
[10 empty] | Total | 1.7137 | 1.3125 | 1.4625
| 3 | total customers
| 26280 | total (customers*8760)
| 1.3125 | total F
| 0.4375 | SAIFI=total F/total customers
| 0.4875 | SAIDI=total G/total customers
| 1.1143 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.5651e-05 | ASUI=1-ASAI
| 1713.75 | ENS=total ENS*1000
| 571.25 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 1.9575 | 3 | 1 | 1.9575 | 0.6525 | 1.9575
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 1.9575 | 3 | 1.5 | 2.9363 | 0.6525 | 1.9575
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 1.9575 | 3 | 1 | 1.9575 | 0.6525 | 1.9575
[10 empty] | Total | 6.8513 | 1.9575 | 5.8725
| 3 | total customers
| 26280 | total (customers*8760)
| 1.9575 | total F
| 0.6525 | SAIFI=total F/total customers
| 1.9575 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99978 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022346 | ASUI=1-ASAI
| 6851.25 | ENS=total ENS*1000
| 2283.75 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.42 |  | 1.26 | 3 | 1 | 1.26 | 0.42 | 1.26
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 1.3275 | 3 | 1.5 | 1.9912 | 0.4425 | 1.3275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 16 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.45 |  | 1.35 | 3 | 1 | 1.35 | 0.45 | 1.35
[10 empty] | Total | 4.6013 | 1.3125 | 3.9375
| 3 | total customers
| 26280 | total (customers*8760)
| 1.3125 | total F
| 0.4375 | SAIFI=total F/total customers
| 1.3125 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014983 | ASUI=1-ASAI
| 4601.25 | ENS=total ENS*1000
| 1533.75 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 18 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | Calculation |  |  | 0.6525 |  | 0.55125 | 0.84483 | 1 | 0.55125 | 0.6525 | 0.55125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | Calculation |  |  | 0.6525 |  | 0.6075 | 0.93103 | 1.5 | 0.91125 | 0.6525 | 0.6075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 0.62625 | 0.95977 | 1 | 0.62625 | 0.6525 | 0.62625
[10 empty] | Total | 2.0888 | 1.9575 | 1.785
| 3 | total customers
| 26280 | total (customers*8760)
| 1.9575 | total F
| 0.6525 | SAIFI=total F/total customers
| 0.595 | SAIDI=total G/total customers
| 0.91188 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.7922e-05 | ASUI=1-ASAI
| 2088.75 | ENS=total ENS*1000
| 696.25 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 8 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 18 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | Calculation |  |  | 0.6525 |  | 0.85125 | 1.3046 | 1 | 0.85125 | 0.6525 | 0.85125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 9 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | Calculation |  |  | 0.6525 |  | 1.4325 | 2.1954 | 1.5 | 2.1488 | 0.6525 | 1.4325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 10 | 1 | 13 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 15 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 17 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 14 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 16 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 18 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | Calculation |  |  | 0.6525 |  | 1.9575 | 3 | 1 | 1.9575 | 0.6525 | 1.9575
[10 empty] | Total | 4.9575 | 1.9575 | 4.2413
| 3 | total customers
| 26280 | total (customers*8760)
| 1.9575 | total F
| 0.6525 | SAIFI=total F/total customers
| 1.4138 | SAIDI=total G/total customers
| 2.1667 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016139 | ASUI=1-ASAI
| 4957.5 | ENS=total ENS*1000
| 1652.5 | AENS=ENS/total customers

## F3_(11-17)
[7 empty] | CASE A | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 5507.4937
0.15 | 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 37586.5875
0.15 |  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | C | 10676.1375
0.15 |  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 9914.3062
0.15 |  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 5507.4937
0.15 |  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 24590.5562
0.15 |  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
0.15 |  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | Calculation |  |  | 0.7525 |  | 1.6262 | 2.1611 | 0.545 | 0.88631 | 165.55 | 357.775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 1.6038 | 2.1527 | 0.545 | 0.87404 | 163.9 | 352.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 1.6038 | 2.1527 | 0.545 | 0.87404 | 163.9 | 352.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.5362 | 1.8398 | 0.5 | 0.76812 | 167 | 307.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.6038 | 1.9207 | 0.5 | 0.80188 | 167 | 320.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.6038 | 1.9207 | 0.415 | 0.66556 | 8.35 | 16.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.5362 | 1.8398 | 0.415 | 0.63754 | 8.35 | 15.3625
[10 empty] | Total | 5.5075 | 844.05 | 1722.825
| 1080 | total customers
| 9460800 | total (customers*8760)
| 844.05 | total F
| 0.78153 | SAIFI=total F/total customers
| 1.5952 | SAIDI=total G/total customers
| 2.0411 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001821 | ASUI=1-ASAI
| 5507.4937 | ENS=total ENS*1000
| 5.0995 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.545 | 5.9119 | 436.15 | 2386.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.545 | 5.9119 | 436.15 | 2386.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.545 | 5.9119 | 436.15 | 2386.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.5 | 5.4238 | 396.5 | 2169.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.5 | 5.4238 | 396.5 | 2169.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.415 | 4.5017 | 19.825 | 108.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.415 | 4.5017 | 19.825 | 108.475
[10 empty] | Total | 37.5866 | 2141.1 | 11715.3
| 1080 | total customers
| 9460800 | total (customers*8760)
| 2141.1 | total F
| 1.9825 | SAIFI=total F/total customers
| 10.8475 | SAIDI=total G/total customers
| 5.4716 | CAIDI=SAIDI/SAIFI
| 0.99876 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012383 | ASUI=1-ASAI
| 37586.5875 | ENS=total ENS*1000
| 34.8024 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7525 |  | 2.9575 | 3.9302 | 0.545 | 1.6118 | 165.55 | 650.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 2.935 | 3.9396 | 0.545 | 1.5996 | 163.9 | 645.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 2.935 | 3.9396 | 0.545 | 1.5996 | 163.9 | 645.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 3.205 | 3.8383 | 0.5 | 1.6025 | 167 | 641
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0 | 0 | 3 | 0
|  |  | 30 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 3.205 | 3.8383 | 0.5 | 1.6025 | 167 | 641
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 3.205 | 3.8383 | 0.415 | 1.3301 | 8.35 | 32.05
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0 | 0 | 3 | 0
|  |  | 22 | 0.75 | 0 | 0 | 3 | 0
|  |  | 24 | 0.75 | 0 | 0 | 3 | 0
|  |  | 25 | 0.6 | 0 | 0 | 3 | 0
|  |  | 27 | 0.75 | 0 | 0 | 3 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 3.205 | 3.8383 | 0.415 | 1.3301 | 8.35 | 32.05
[10 empty] | Total | 10.6761 | 844.05 | 3288.15
| 1080 | total customers
| 9460800 | total (customers*8760)
| 844.05 | total F
| 0.78153 | SAIFI=total F/total customers
| 3.0446 | SAIDI=total G/total customers
| 3.8957 | CAIDI=SAIDI/SAIFI
| 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00034756 | ASUI=1-ASAI
| 10676.1375 | ENS=total ENS*1000
| 9.8853 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 2.2412 | 1.1305 | 0.545 | 1.2215 | 436.15 | 493.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 2.2225 | 1.1211 | 0.545 | 1.2113 | 436.15 | 488.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 3.3975 | 1.7137 | 0.545 | 1.8516 | 436.15 | 747.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 3.3975 | 1.7137 | 0.5 | 1.6987 | 396.5 | 679.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 2.2225 | 1.1211 | 0.5 | 1.1112 | 396.5 | 444.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 3.3975 | 1.7137 | 0.415 | 1.41 | 19.825 | 33.975
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 3.3975 | 1.7137 | 0.415 | 1.41 | 19.825 | 33.975
[10 empty] | Total | 9.9143 | 2141.1 | 2921.425
| 1080 | total customers
| 9460800 | total (customers*8760)
| 2141.1 | total F
| 1.9825 | SAIFI=total F/total customers
| 2.705 | SAIDI=total G/total customers
| 1.3645 | CAIDI=SAIDI/SAIFI
| 0.99969 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00030879 | ASUI=1-ASAI
| 9914.3062 | ENS=total ENS*1000
| 9.1799 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7525 |  | 1.6262 | 2.1611 | 0.545 | 0.88631 | 165.55 | 357.775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 1.6038 | 2.1527 | 0.545 | 0.87404 | 163.9 | 352.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.745 |  | 1.6038 | 2.1527 | 0.545 | 0.87404 | 163.9 | 352.825
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.5362 | 1.8398 | 0.5 | 0.76812 | 167 | 307.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.6038 | 1.9207 | 0.5 | 0.80188 | 167 | 320.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.6038 | 1.9207 | 0.415 | 0.66556 | 8.35 | 16.0375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0 | 0
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.835 |  | 1.5362 | 1.8398 | 0.415 | 0.63754 | 8.35 | 15.3625
[10 empty] | Total | 5.5075 | 844.05 | 1722.825
| 1080 | total customers
| 9460800 | total (customers*8760)
| 844.05 | total F
| 0.78153 | SAIFI=total F/total customers
| 1.5952 | SAIDI=total G/total customers
| 2.0411 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0001821 | ASUI=1-ASAI
| 5507.4937 | ENS=total ENS*1000
| 5.0995 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 11 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 2.5225 | 1.2724 | 0.545 | 1.3748 | 436.15 | 554.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 12 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 25 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 3.9787 | 2.0069 | 0.545 | 2.1684 | 436.15 | 875.325
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 13 | 220 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 6.685 | 3.372 | 0.545 | 3.6433 | 436.15 | 1470.7
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 14 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.9825 |  | 6.685 | 3.372 | 0.5 | 3.3425 | 396.5 | 1337
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 15 | 200 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 30 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.1162 | 5.1028 | 0.5 | 5.0581 | 396.5 | 2023.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 16 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.415 | 4.5017 | 19.825 | 108.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 17 | 10 | 19 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 21 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 23 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 26 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 28 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 20 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 22 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 24 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 25 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 27 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 29 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 30 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.9825 |  | 10.8475 | 5.4716 | 0.415 | 4.5017 | 19.825 | 108.475
[10 empty] | Total | 24.5906 | 2141.1 | 6478.175
| 1080 | total customers
| 9460800 | total (customers*8760)
| 2141.1 | total F
| 1.9825 | SAIFI=total F/total customers
| 5.9983 | SAIDI=total G/total customers
| 3.0256 | CAIDI=SAIDI/SAIFI
| 0.99932 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00068474 | ASUI=1-ASAI
| 24590.5562 | ENS=total ENS*1000
| 22.769 | AENS=ENS/total customers

## F4_(18-25)
[7 empty] | CASE A | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 6407.675
0.15 | 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 48952.075
0.15 |  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 12121.925
0.15 |  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 12837.2
0.15 |  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | E | 6407.675
0.15 |  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | F | 30581.325
0.15 |  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
0.15 |  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
0.15 |  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.545 | 0.84747 | 167.2 | 342.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.5 | 0.7775 | 152 | 311
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.5 | 0.81125 | 156.5 | 324.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.415 | 0.67334 | 7.825 | 16.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.415 | 0.64532 | 7.6 | 15.55
[10 empty] | Total | 6.4077 | 1007.575 | 2080.225
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1007.575 | total F
| 0.77506 | SAIFI=total F/total customers
| 1.6002 | SAIDI=total G/total customers
| 2.0646 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018267 | ASUI=1-ASAI
| 6407.675 | ENS=total ENS*1000
| 4.929 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.545 | 6.6531 | 484.55 | 2685.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.545 | 6.6531 | 484.55 | 2685.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.545 | 6.6531 | 484.55 | 2685.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.545 | 6.6531 | 484.55 | 2685.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.5 | 6.1037 | 440.5 | 2441.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.5 | 6.1037 | 440.5 | 2441.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.415 | 5.0661 | 22.025 | 122.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.415 | 5.0661 | 22.025 | 122.075
[10 empty] | Total | 48.9521 | 2863.25 | 15869.75
| 1300 | total customers
| 11388000 | total (customers*8760)
| 2863.25 | total F
| 2.2025 | SAIFI=total F/total customers
| 12.2075 | SAIDI=total G/total customers
| 5.5426 | CAIDI=SAIDI/SAIFI
| 0.99861 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0013936 | ASUI=1-ASAI
| 48952.075 | ENS=total ENS*1000
| 37.6554 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.545 | 1.6609 | 172.15 | 670.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.545 | 1.6241 | 167.2 | 655.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.545 | 1.6609 | 172.15 | 670.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.545 | 1.6609 | 172.15 | 670.45
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.5 | 1.49 | 152 | 596
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.5 | 1.5237 | 156.5 | 609.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 3.0475 | 3.8946 | 0.415 | 1.2647 | 7.825 | 30.475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 3 | 0
|  |  | 35 | 0.75 | 0 | 0 | 3 | 0
|  |  | 37 | 0.75 | 0 | 0 | 3 | 0
|  |  | 38 | 0.6 | 0 | 0 | 3 | 0
|  |  | 40 | 0.75 | 0 | 0 | 3 | 0
|  |  | 42 | 0.75 | 0 | 0 | 3 | 0
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.415 | 1.2367 | 7.6 | 29.8
[10 empty] | Total | 12.1219 | 1007.575 | 3932.725
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1007.575 | total F
| 0.77506 | SAIFI=total F/total customers
| 3.0252 | SAIDI=total G/total customers
| 3.9032 | CAIDI=SAIDI/SAIFI
| 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00034534 | ASUI=1-ASAI
| 12121.925 | ENS=total ENS*1000
| 9.3246 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 2.3325 | 1.059 | 0.545 | 1.2712 | 484.55 | 513.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.545 | 1.9116 | 484.55 | 771.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.545 | 1.9116 | 484.55 | 771.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.545 | 1.9116 | 484.55 | 771.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.5 | 1.7537 | 440.5 | 701.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 2.3325 | 1.059 | 0.5 | 1.1662 | 440.5 | 466.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.415 | 1.4556 | 22.025 | 35.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 3.5075 | 1.5925 | 0.415 | 1.4556 | 22.025 | 35.075
[10 empty] | Total | 12.8372 | 2863.25 | 4066.25
| 1300 | total customers
| 11388000 | total (customers*8760)
| 2863.25 | total F
| 2.2025 | SAIFI=total F/total customers
| 3.1279 | SAIDI=total G/total customers
| 1.4202 | CAIDI=SAIDI/SAIFI
| 0.99964 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00035706 | ASUI=1-ASAI
| 12837.2 | ENS=total ENS*1000
| 9.8748 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.545 | 0.84747 | 167.2 | 342.1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.545 | 0.88426 | 172.15 | 356.95
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.1 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.1 | 0
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.5 | 0.7775 | 152 | 311
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.5 | 0.81125 | 156.5 | 324.5
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.7825 |  | 1.6225 | 2.0735 | 0.415 | 0.67334 | 7.825 | 16.225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0 | 0 | 3 | 0
|  |  | 34 | 0.6 | 0 | 0 | 0.5
|  |  | 35 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.555 | 2.0461 | 0.415 | 0.64532 | 7.6 | 15.55
[10 empty] | Total | 6.4077 | 1007.575 | 2080.225
| 1300 | total customers
| 11388000 | total (customers*8760)
| 1007.575 | total F
| 0.77506 | SAIFI=total F/total customers
| 1.6002 | SAIDI=total G/total customers
| 2.0646 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018267 | ASUI=1-ASAI
| 6407.675 | ENS=total ENS*1000
| 4.929 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 18 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 2.6325 | 1.1952 | 0.545 | 1.4347 | 484.55 | 579.15
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 19 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 5.3387 | 2.424 | 0.545 | 2.9096 | 484.55 | 1174.525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 20 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 38 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 5.3387 | 2.424 | 0.545 | 2.9096 | 484.55 | 1174.525
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 21 | 220 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 8.045 | 3.6527 | 0.545 | 4.3845 | 484.55 | 1769.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 22 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 8.045 | 3.6527 | 0.5 | 4.0225 | 440.5 | 1609
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 23 | 200 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 43 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 2.2025 |  | 9.5763 | 4.3479 | 0.5 | 4.7881 | 440.5 | 1915.25
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 24 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.415 | 5.0661 | 22.025 | 122.075
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 25 | 10 | 31 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 33 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 36 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 39 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 41 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 32 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 34 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 35 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 37 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 38 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 40 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 42 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 43 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 2.2025 |  | 12.2075 | 5.5426 | 0.415 | 5.0661 | 22.025 | 122.075
[10 empty] | Total | 30.5813 | 2863.25 | 8466.5
| 1300 | total customers
| 11388000 | total (customers*8760)
| 2863.25 | total F
| 2.2025 | SAIFI=total F/total customers
| 6.5127 | SAIDI=total G/total customers
| 2.957 | CAIDI=SAIDI/SAIFI
| 0.99926 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00074346 | ASUI=1-ASAI
| 30581.325 | ENS=total ENS*1000
| 23.5241 | AENS=ENS/total customers

## F5_(26-28)
[7 empty] | CASE A & E | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1451.25
0.15 | 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | B | 5805
0.15 |  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | C | 3870
0.15 |  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | D | 1773.75
0.15 |  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375 | [5 empty] | E | 1451.25
0.15 |  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 4267.5
0.15 |  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | Calculation |  |  | 0.435 |  | 0.49875 | 1.1466 | 1 | 0.49875 | 0.435 | 0.49875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 0.52125 | 1.178 | 1 | 0.52125 | 0.4425 | 0.52125
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.4125 |  | 0.43125 | 1.0455 | 1 | 0.43125 | 0.4125 | 0.43125
[10 empty] | Total | 1.4512 | 1.29 | 1.4512
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 0.48375 | SAIDI=total G/total customers
| 1.125 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.5223e-05 | ASUI=1-ASAI
| 1451.25 | ENS=total ENS*1000
| 483.75 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
[10 empty] | Total | 5.805 | 1.935 | 5.805
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 1.935 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99978 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022089 | ASUI=1-ASAI
| 5805 | ENS=total ENS*1000
| 1935 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.435 |  | 1.305 | 3 | 1 | 1.305 | 0.435 | 1.305
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 1.3275 | 3 | 1 | 1.3275 | 0.4425 | 1.3275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 47 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.4125 |  | 1.2375 | 3 | 1 | 1.2375 | 0.4125 | 1.2375
[10 empty] | Total | 3.87 | 1.29 | 3.87
| 3 | total customers
| 26280 | total (customers*8760)
| 1.29 | total F
| 0.43 | SAIFI=total F/total customers
| 1.29 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00014726 | ASUI=1-ASAI
| 3870 | ENS=total ENS*1000
| 1290 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 49 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.60375 | 0.93605 | 1 | 0.60375 | 0.645 | 0.60375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.6225 | 0.96512 | 1 | 0.6225 | 0.645 | 0.6225
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 47 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 0.5475 | 0.84884 | 1 | 0.5475 | 0.645 | 0.5475
[10 empty] | Total | 1.7738 | 1.935 | 1.7738
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 0.59125 | SAIDI=total G/total customers
| 0.91667 | CAIDI=SAIDI/SAIFI
| 0.99993 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.7494e-05 | ASUI=1-ASAI
| 1773.75 | ENS=total ENS*1000
| 591.25 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 26 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 49 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.90375 | 1.4012 | 1 | 0.90375 | 0.645 | 0.90375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 27 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 1.4287 | 2.2151 | 1 | 1.4287 | 0.645 | 1.4287
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 28 | 1 | 44 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 46 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 48 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 45 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 47 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 49 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
[10 empty] | Total | 4.2675 | 1.935 | 4.2675
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 1.4225 | SAIDI=total G/total customers
| 2.2054 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00016239 | ASUI=1-ASAI
| 4267.5 | ENS=total ENS*1000
| 1422.5 | AENS=ENS/total customers

## F6_(29-31)
[7 empty] | CASE A & E | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 1629.375
0.15 | 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 6772.5
0.15 |  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | C | 4713.75
0.15 |  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06 | [5 empty] | D | 1972.5
0.15 |  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27 | [5 empty] | E | 1629.375
0.15 |  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0 | [5 empty] | F | 5141.25
0.15 |  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | Calculation |  |  | 0.4425 |  | 0.44625 | 1.0085 | 1 | 0.44625 | 0.4425 | 0.44625
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.465 |  | 0.51375 | 1.1048 | 1 | 0.51375 | 0.465 | 0.51375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.4425 |  | 0.44625 | 1.0085 | 1.5 | 0.66938 | 0.4425 | 0.44625
[10 empty] | Total | 1.6294 | 1.35 | 1.4062
| 3 | total customers
| 26280 | total (customers*8760)
| 1.35 | total F
| 0.45 | SAIFI=total F/total customers
| 0.46875 | SAIDI=total G/total customers
| 1.0417 | CAIDI=SAIDI/SAIFI
| 0.99995 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 5.351e-05 | ASUI=1-ASAI
| 1629.375 | ENS=total ENS*1000
| 543.125 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1 | 1.935 | 0.645 | 1.935
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1.5 | 2.9025 | 0.645 | 1.935
[10 empty] | Total | 6.7725 | 1.935 | 5.805
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 1.935 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99978 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00022089 | ASUI=1-ASAI
| 6772.5 | ENS=total ENS*1000
| 2257.5 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.4425 |  | 1.3275 | 3 | 1 | 1.3275 | 0.4425 | 1.3275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | Calculation |  |  | 0.465 |  | 1.395 | 3 | 1 | 1.395 | 0.465 | 1.395
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 53 | 0.75 | 0 | 0 | 0.5 | 0
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.4425 |  | 1.3275 | 3 | 1.5 | 1.9913 | 0.4425 | 1.3275
[10 empty] | Total | 4.7138 | 1.35 | 4.05
| 3 | total customers
| 26280 | total (customers*8760)
| 1.35 | total F
| 0.45 | SAIFI=total F/total customers
| 1.35 | SAIDI=total G/total customers
| 3 | CAIDI=SAIDI/SAIFI
| 0.99985 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015411 | ASUI=1-ASAI
| 4713.75 | ENS=total ENS*1000
| 1571.25 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 55 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.5475 | 0.84884 | 1 | 0.5475 | 0.645 | 0.5475
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.60375 | 0.93605 | 1 | 0.60375 | 0.645 | 0.60375
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 0.5475 | 0.84884 | 1.5 | 0.82125 | 0.645 | 0.5475
[10 empty] | Total | 1.9725 | 1.935 | 1.6987
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 0.56625 | SAIDI=total G/total customers
| 0.87791 | CAIDI=SAIDI/SAIFI
| 0.99994 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 6.464e-05 | ASUI=1-ASAI
| 1972.5 | ENS=total ENS*1000
| 657.5 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 29 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 55 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 0.82875 | 1.2849 | 1 | 0.82875 | 0.645 | 0.82875
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 30 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | Calculation |  |  | 0.645 |  | 1.41 | 2.186 | 1 | 1.41 | 0.645 | 1.41
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 31 | 1 | 50 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 52 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 54 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 51 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 53 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 55 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | Calculation |  |  | 0.645 |  | 1.935 | 3 | 1.5 | 2.9025 | 0.645 | 1.935
[10 empty] | Total | 5.1412 | 1.935 | 4.1738
| 3 | total customers
| 26280 | total (customers*8760)
| 1.935 | total F
| 0.645 | SAIFI=total F/total customers
| 1.3913 | SAIDI=total G/total customers
| 2.157 | CAIDI=SAIDI/SAIFI
| 0.99984 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00015882 | ASUI=1-ASAI
| 5141.25 | ENS=total ENS*1000
| 1713.75 | AENS=ENS/total customers

## F7_(32-38)
[7 empty] | CASE A | [6 empty] | ENS
0.15 | Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B | A | 5728.45
0.15 | 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | B | 39077.65
0.15 |  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045 | [5 empty] | C | 11193.25
0.15 |  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | D | 10389.15
0.15 |  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | E | 5728.45
0.15 |  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625 | [5 empty] | F | 24896.5875
0.15 |  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
0.15 |  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
0.15 |  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
0.15 |  |  | x former |  |  | 0.1 | 10 | 1
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | x former |  |  | 0 | 0 | 0
0.15 |  |  | Calculation |  |  | 0.76 |  | 1.63 | 2.1447 | 0.545 | 0.88835 | 167.2 | 358.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.63 | 2.1447 | 0.545 | 0.88835 | 167.2 | 358.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.73 |  | 1.54 | 2.1096 | 0.545 | 0.8393 | 160.6 | 338.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.63 | 1.9176 | 0.545 | 0.88835 | 187 | 358.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.54 | 1.8118 | 0.5 | 0.77 | 170 | 308
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.63 | 1.9176 | 0.5 | 0.815 | 170 | 326
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.54 | 1.8118 | 0.415 | 0.6391 | 8.5 | 15.4
[10 empty] | Total | 5.7284 | 1030.5 | 2064
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1030.5 | total F
| 0.79884 | SAIFI=total F/total customers
| 1.6 | SAIDI=total G/total customers
| 2.0029 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018265 | ASUI=1-ASAI
| 5728.45 | ENS=total ENS*1000
| 4.4407 | AENS=ENS/total customers
CASE B
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.545 | 5.9242 | 437.8 | 2391.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.545 | 5.9242 | 437.8 | 2391.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.545 | 5.9242 | 437.8 | 2391.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.545 | 5.9242 | 437.8 | 2391.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.5 | 5.435 | 398 | 2174
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.5 | 5.435 | 398 | 2174
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.415 | 4.511 | 19.9 | 108.7
[10 empty] | Total | 39.0776 | 2567.1 | 14022.3
| 1290 | total customers
| 11300400 | total (customers*8760)
| 2567.1 | total F
| 1.99 | SAIFI=total F/total customers
| 10.87 | SAIDI=total G/total customers
| 5.4623 | CAIDI=SAIDI/SAIFI
| 0.99876 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.0012409 | ASUI=1-ASAI
| 39077.65 | ENS=total ENS*1000
| 30.2928 | AENS=ENS/total customers
CASE C
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.545 | 1.6241 | 167.2 | 655.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 2.98 | 3.9211 | 0.545 | 1.6241 | 167.2 | 655.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.73 |  | 2.89 | 3.9589 | 0.545 | 1.575 | 160.6 | 635.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 3.25 | 3.8235 | 0.545 | 1.7712 | 187 | 715
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0 | 0 | 3 | 0
|  |  | 67 | 0.6 | 0 | 0 | 3 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 3.25 | 3.8235 | 0.5 | 1.625 | 170 | 650
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 3.25 | 3.8235 | 0.5 | 1.625 | 170 | 650
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0 | 0 | 3 | 0
|  |  | 59 | 0.8 | 0 | 0 | 3 | 0
|  |  | 61 | 0.6 | 0 | 0 | 3 | 0
|  |  | 62 | 0.8 | 0 | 0 | 3 | 0
|  |  | 64 | 0.6 | 0 | 0 | 3 | 0
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 3.25 | 3.8235 | 0.415 | 1.3487 | 8.5 | 32.5
[10 empty] | Total | 11.1932 | 1030.5 | 3994.5
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1030.5 | total F
| 0.79884 | SAIFI=total F/total customers
| 3.0965 | SAIDI=total G/total customers
| 3.8763 | CAIDI=SAIDI/SAIFI
| 0.99965 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00035348 | ASUI=1-ASAI
| 11193.25 | ENS=total ENS*1000
| 8.6769 | AENS=ENS/total customers
CASE D
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 2.245 | 1.1281 | 0.545 | 1.2235 | 437.8 | 493.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 2.245 | 1.1281 | 0.545 | 1.2235 | 437.8 | 493.9
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 3.42 | 1.7186 | 0.545 | 1.8639 | 437.8 | 752.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 3.42 | 1.7186 | 0.545 | 1.8639 | 437.8 | 752.4
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 2.17 | 1.0905 | 0.5 | 1.085 | 398 | 434
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 3.42 | 1.7186 | 0.5 | 1.71 | 398 | 684
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 3.42 | 1.7186 | 0.415 | 1.4193 | 19.9 | 34.2
[10 empty] | Total | 10.3891 | 2567.1 | 3644.8
| 1290 | total customers
| 11300400 | total (customers*8760)
| 2567.1 | total F
| 1.99 | SAIFI=total F/total customers
| 2.8254 | SAIDI=total G/total customers
| 1.4198 | CAIDI=SAIDI/SAIFI
| 0.99968 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00032254 | ASUI=1-ASAI
| 10389.15 | ENS=total ENS*1000
| 8.0536 | AENS=ENS/total customers
CASE E
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.63 | 2.1447 | 0.545 | 0.88835 | 167.2 | 358.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.76 |  | 1.63 | 2.1447 | 0.545 | 0.88835 | 167.2 | 358.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.73 |  | 1.54 | 2.1096 | 0.545 | 0.8393 | 160.6 | 338.8
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.63 | 1.9176 | 0.545 | 0.88835 | 187 | 358.6
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.54 | 1.8118 | 0.5 | 0.77 | 170 | 308
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0 | 0
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.63 | 1.9176 | 0.5 | 0.815 | 170 | 326
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 0.5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 0.5 | 0
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0 | 0
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | Calculation |  |  | 0.85 |  | 1.54 | 1.8118 | 0.415 | 0.6391 | 8.5 | 15.4
[10 empty] | Total | 5.7284 | 1030.5 | 2064
| 1290 | total customers
| 11300400 | total (customers*8760)
| 1030.5 | total F
| 0.79884 | SAIFI=total F/total customers
| 1.6 | SAIDI=total G/total customers
| 2.0029 | CAIDI=SAIDI/SAIFI
| 0.99982 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00018265 | ASUI=1-ASAI
| 5728.45 | ENS=total ENS*1000
| 4.4407 | AENS=ENS/total customers
CASE F
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 32 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 2.5262 | 1.2695 | 0.545 | 1.3768 | 437.8 | 555.775
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 33 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 62 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 4.0012 | 2.0107 | 0.545 | 2.1807 | 437.8 | 880.275
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 34 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 6.7075 | 3.3706 | 0.545 | 3.6556 | 437.8 | 1475.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 35 | 220 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 6.7075 | 3.3706 | 0.545 | 3.6556 | 437.8 | 1475.65
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 36 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 0.5 | 0.05625
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 0.5 | 0.06
|  |  | 67 | 0.6 | 0.15 | 0.09 | 0.5 | 0.045
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | x former |  |  | 0.1 | 0.5 | 0.05
|  |  | Calculation |  |  | 1.99 |  | 8.1638 | 4.1024 | 0.5 | 4.0819 | 398 | 1632.75
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 37 | 200 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.5 | 5.435 | 398 | 2174
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OG*B | G=OI*B
| 38 | 10 | 56 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 58 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 60 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 63 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 65 | 0.75 | 0.15 | 0.1125 | 3 | 0.3375
|  |  | 57 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 59 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 61 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 62 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 64 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | 66 | 0.8 | 0.15 | 0.12 | 3 | 0.36
|  |  | 67 | 0.6 | 0.15 | 0.09 | 3 | 0.27
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | x former |  |  | 0.1 | 10 | 1
|  |  | Calculation |  |  | 1.99 |  | 10.87 | 5.4623 | 0.415 | 4.511 | 19.9 | 108.7
[10 empty] | Total | 24.8966 | 2567.1 | 8302.8
| 1290 | total customers
| 11300400 | total (customers*8760)
| 2567.1 | total F
| 1.99 | SAIFI=total F/total customers
| 6.4363 | SAIDI=total G/total customers
| 3.2343 | CAIDI=SAIDI/SAIFI
| 0.99927 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00073474 | ASUI=1-ASAI
| 24896.5875 | ENS=total ENS*1000
| 19.2997 | AENS=ENS/total customers

## ENS_Deviation
Feeder Number | Case A_ENS |  | Case B_ENS |  | Case C_ENS |  | Case D_ENS |  | Case E_ENS |  | Case F_ENS
| Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer | Feeder | Customer
Feeder 1 | 5616.675 | 1100 | 38390.625 | 1100 | 10486.8 | 1100 | 10136.0625 | 1100 | 5616.675 | 1100 | 24178.9063 | 1100
Feeder 2 | 1713.8 | 3 | 6851.3 | 3 | 4601.3 | 3 | 2088.8 | 3 | 1713.8 | 3 | 4957.5 | 3
Feeder 3 | 5507.4937 | 1080 | 37586.5875 | 1080 | 10676.1375 | 1080 | 9914.3062 | 1080 | 5507.4937 | 1080 | 24590.5563 | 1080
Feeder 4 | 6407.675 | 1300 | 48952.08 | 1300 | 12121.93 | 1300 | 12837.2 | 1300 | 6407.675 | 1300 | 30581.33 | 1300
Feeder 5 | 1451.25 | 3 | 5805 | 3 | 3870 | 3 | 1773.75 | 3 | 1451.25 | 3 | 4267.5 | 3
Feeder 6 | 1629.375 | 3 | 6772.5 | 3 | 4713.75 | 3 | 1972.5 | 3 | 1629.375 | 3 | 5141.25 | 3
Feeder 7 | 5728.45 | 1290 | 39077.65 | 1290 | 11193.25 | 1290 | 10389.15 | 1290 | 5728.45 | 1290 | 24896.59 | 1290
TOTAL | 28054.7188 | 4779 | 183435.7425 | 4779 | 57663.1675 | 4779 | 49111.7687 | 4779 | 28054.7188 | 4779 | 118613.6326 | 4779
Analytic | 28.0547 |  | 183.4357 |  | 57.6632 |  | 49.1118 |  | 28.0547 |  | 118.6136
Monte Carlo_Code | 28.052 |  | 183.36 |  | 56.505 |  | 49.069 |  | 28.051 |  | 117.74
Deviation | 0.0096909 |  | 0.041291 |  | 2.0085 |  | 0.087085 |  | 0.013255 |  | 0.73654
| CASE A | [5 empty] | CASE B
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 184000 | 28.023 | 28.049 | 28.052 | 28.082 |  | 945000 | 183.21 | 183.48 | 183.49 | 183.36
| CASE C | [5 empty] | CASE D
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 185000 | 56.498 | 56.494 | 56.495 | 56.505 |  | 47500 | 48.961 | 49.082 | 49.069 | 49.123
| CASE E | [5 empty] | CASE F
| N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001 |  | N2\\\\\\\\\\\\Eps | 0.03 | 0.01 | 0.05 | 0.001
| 32500 | 28.064 | 28.033 | 28.051 | 27.947 |  | 1140000 | 117.52 | 117.59 | 117.61 | 117.74