## Case 1
F1 | main | length | failure rate | length*failure rate | comp repair | unavail |  |  | F1 | main | length | failure rate | length*failure rate | comp repair | unavail |  |  | F1 | main | length | failure rate | length*failure rate |  | comp repair | unavail | repair | F1 | main | length | failure rate | length*failure rate | comp repair | unavail
| 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  |  | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  |  | 1 | 0.75 | 0.065 | 0.04875 |  | 1 | 0.04875 |  |  | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
| 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 3 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052 |  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
LP7 | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | LP1 | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | LP4 | 5 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052 |  | LP5 | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
| 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  |  | 7 | 0.75 | 0.065 | 0.04875 |  | 1 | 0.04875 |  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
| 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 10 | 0.6 | 0.065 | 0.039 |  | 1 | 0.039 |  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
lateral | 12 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375 |  |  | lateral | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195 |  |  | lateral | 8 | 0.8 | 0.065 | 0.052 |  | 5 | 0.26 |  | lateral | 9 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | x former | 0.015 | 10 | 0.15 | [5 empty] | x former | 0.015 | 200 | 3 | [5 empty] | x former | 0.015 |  | 10 | 0.15 |  |  |  |  | x former | 0.015 | 200 | 3
|  |  |  | 0.30425 |  | 0.63425 | 2.0846 | [5 empty] | 0.2945 |  | 3.4355 | 1.9881 | [5 empty] | 0.3075 |  |  | 0.6505 | 2.1154 |  |  |  |  | 0.30425 |  | 3.4843
F2 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | F2 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052 | [11 empty] | F3 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
| 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052 | [12 empty] | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
LP9 | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  | LP10 | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039 | [12 empty] | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
| 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375 |  |  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26 | [12 empty] | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  |  | 0.19175 |  | 0.38675 | 2.0169 | [5 empty] | 0.195 |  | 0.403 | 2.0667 | [10 empty] | LP13 | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[27 empty] | lateral | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
[30 empty] | x former | 0.015 | 200 | 3
F3 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  | F3 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  | F3 | 19 | 0.75 | 0.065 | 0.04875 |  | 1 | 0.04875 | [5 empty] | 0.2945 |  | 3.4745
| 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 21 | 0.6 | 0.065 | 0.039 |  | 1 | 0.039
| 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 23 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
| 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 26 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052 |  | F3 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
LP11 | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  | LP17 | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  | LP15 | 28 | 0.6 | 0.065 | 0.039 |  | 1 | 0.039 |  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
| 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26 |  |  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195 |  |  |  | 27 | 0.75 | 0.065 | 0.04875 |  | 5 | 0.24375 |  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | x former | 0.015 | 10 | 0.15 | [5 empty] | x former | 0.015 | 10 | 0.15 | [5 empty] | x former | 0.015 |  | 10 | 0.15 |  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  |  | 0.29775 |  | 0.64075 | 2.152 | [5 empty] | 0.28475 |  | 0.57575 | 2.0219 | [5 empty] | 0.2945 |  |  | 0.6245 | 2.1205 | LP17 | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[27 empty] | lateral | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[30 empty] | x former | 0.015 | 200 | 3
F4 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | F4 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  | F4 | 31 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052 | [6 empty] | 0.28475 |  | 3.4257
| 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | 33 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
| 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | 36 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052 |  |  | F4 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
| 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | 39 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052 |  |  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
LP19 | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  | LP25 | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  | LP23 | 41 | 0.6 | 0.065 | 0.039 |  | 1 | 0.039 |  |  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
| 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195 |  |  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195 |  |  | 40 | 0.75 | 0.065 | 0.04875 |  | 5 | 0.24375 |  |  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | xformer | 0.015 | 10 | 0.15 | [5 empty] | xformer | 0.015 | 200 | 3 |  |  |  |  | xformer | 0.015 |  | 10 | 0.15 |  |  | LP21 | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  |  | 0.301 |  | 0.592 | 1.9668 | [5 empty] | 0.301 |  | 3.442 | 1.9668 |  |  |  |  | 0.31075 |  |  | 0.64075 | 2.0619 |  | lateral | 37 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
F5 | [8 empty] | F5 | [20 empty] | xformer | 0.015 | 200 | 3
| 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052 | [15 empty] | 0.31075 |  | 3.4908 | 1.9668
| 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
LP26 | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  | LP28 | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
| 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375 |  |  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  |  | 0.1885 |  | 0.3835 | 2.0345 | [5 empty] | 0.17875 |  | 0.33475 | 1.8727
L. Goel
F6
[10 empty] | 50 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[10 empty] | 52 | 0.8 | 0.065 | 0.052 | 1 | 0.052
[9 empty] | LP31 | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
[9 empty] | Lateral | 55 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[13 empty] | 0.19175 |  | 0.34775 | 1.8727
[9 empty] | F7 | main | length | failure rate | length*failure rate | comp repair | unavail
[10 empty] | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[10 empty] | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[9 empty] | LP35 | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[10 empty] | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[10 empty] | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[9 empty] | lateral | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
[12 empty] | x former | 0.015 | 200 | 3
[13 empty] | 0.301 |  | 3.494
[9 empty] | F7 | main | length | failure rate | length*failure rate | comp repair | unavail
[10 empty] | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[10 empty] | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[9 empty] | LP38 | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[10 empty] | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[10 empty] | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
[9 empty] | lateral | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[12 empty] | x former | 0.015 | 200 | 3
[13 empty] | 0.288 |  | 3.429

## Case 2
F1 | main | length | failure rate | length*failure rate | comp repair | unavail |  | F1 | main | length | failure rate | length*failure rate | comp repair | unavail | F1 | main | length | failure rate | length*failure rate | comp repair | unavail
LP1-7 |  |  | 0.0035 | 0.0058
|  |  | 0.0035 | 0.0058
|  |  | 0.0035 | 0.0058
|  |  | 0.001 | 0.001
|  |  | 0.015 | 0.015
|  |  | 0.015 | 0.015
|  |  | 0.0015 | 0.002
|  |  | 0.0015 | 0.002
|  |  | 0.001 | 0.001
|  |  | 0.004 | 0.006
[6 empty] | 0.0588 | -0.0006
0.0594

## Case 3
F1 | main | length | failure rate | length*failure rate | comp repair | unavail |  |  | F1 | main | length | failure rate | length*failure rate | comp repair | unavail |  |  | F1 | main | length | failure rate | length*failure rate |  | comp repair | unavail
| 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  |  | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  |  | 1 | 0.75 | 0.065 | 0.04875 |  | 1 | 0.04875
| 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 3 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
LP7 | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | LP1 | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | LP4 | 5 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
| 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  |  | 7 | 0.75 | 0.065 | 0.04875 |  | 1 | 0.04875
| 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 10 | 0.6 | 0.065 | 0.039 |  | 1 | 0.039
lateral | 12 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375 |  |  | lateral | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195 |  |  | lateral | 8 | 0.8 | 0.065 | 0.052 |  | 5 | 0.26
|  |  | x former | 0.015 | 10 | 0.15 | [5 empty] | x former | 0.015 | 200 | 3 | [5 empty] | x former | 0.015 |  | 10 | 0.15
|  |  |  | 0.30425 |  | 0.63425 | 2.0846 | [5 empty] | 0.2945 |  | 3.4355 | 1.9881 | [5 empty] | 0.3075 |  |  | 0.6505 | 2.1154
F2 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | F2 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052
| 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052
LP9 | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  | LP10 | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
| 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375 |  |  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  |  | 0.19175 |  | 0.38675 | 2.0169 | [5 empty] | 0.195 |  | 0.403 | 2.0667
F3 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  | F3 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  | F3 | 19 | 0.75 | 0.065 | 0.04875 |  | 1 | 0.04875
| 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 21 | 0.6 | 0.065 | 0.039 |  | 1 | 0.039
| 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 23 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
| 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 26 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
LP11 | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  | LP17 | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  | LP15 | 28 | 0.6 | 0.065 | 0.039 |  | 1 | 0.039
| 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26 |  |  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195 |  |  |  | 27 | 0.75 | 0.065 | 0.04875 |  | 5 | 0.24375
|  |  | x former | 0.015 | 10 | 0.15 | [5 empty] | x former | 0.015 | 10 | 0.15 | [5 empty] | x former | 0.015 |  | 10 | 0.15
|  |  |  | 0.29775 |  | 0.64075 | 2.152 | [5 empty] | 0.28475 |  | 0.57575 | 2.0219 | [5 empty] | 0.2945 |  |  | 0.6245 | 2.1205
F4 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | F4 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  | F4 | 31 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
| 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | 33 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
| 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | 36 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
| 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  | 39 | 0.8 | 0.065 | 0.052 |  | 1 | 0.052
LP19 | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  | LP25 | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  | LP23 | 41 | 0.6 | 0.065 | 0.039 |  | 1 | 0.039
| 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195 |  |  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195 |  |  | 40 | 0.75 | 0.065 | 0.04875 |  | 5 | 0.24375
|  |  | xformer | 0.015 | 10 | 0.15 | [5 empty] | xformer | 0.015 | 10 | 0.15 |  |  |  |  | xformer | 0.015 |  | 10 | 0.15
|  |  |  | 0.301 |  | 0.592 | 1.9668 | [5 empty] | 0.301 |  | 0.592 | 1.9668 |  |  |  |  | 0.31075 |  |  | 0.64075 | 2.0619
F5 | [8 empty] | F5
| 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052 |  |  |  | 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052
| 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039 |  |  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
LP26 | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875 |  |  | LP28 | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
| 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375 |  |  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  |  | 0.1885 |  | 0.3835 | 2.0345 | [5 empty] | 0.17875 |  | 0.33475 | 1.8727
L. Goel

## F1
CASE A_F1
| Load Point | Customers | Main | Length | Failure Rate | E*F | Reapir Time | Unavailability | Overall Repair time | Average Load | ENS=OK*OI | F=OF*B | G=OH*B
| 1 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 3.4355 | 11.6655 | 0.545 | 1.8723 | 64.79 | 755.81
| 2 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 3.4843 | 11.4519 | 0.545 | 1.8989 | 66.935 | 766.535
| 3 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 3.4355 | 11.6655 | 0.545 | 1.8723 | 64.79 | 755.81
| 4 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.3075 |  | 3.5005 | 11.3837 | 0.545 | 1.9078 | 67.65 | 770.11
| 5 | 200 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 9 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 3.4843 | 11.4519 | 0.5 | 1.7421 | 60.85 | 696.85
| 6 | 10 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.3075 |  | 3.5005 | 11.3837 | 0.415 | 1.4527 | 3.075 | 35.005
| 7 | 10 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 12 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 3.4843 | 11.4519 | 0.415 | 1.446 | 3.0425 | 34.8425
[11 empty] | 12.1922 | 331.1325 | 3814.9625
| 1100 | total customers
| 9636000 | total (customers*8760)
| 331.1325 | total F
| 0.30103 | SAIFI=total F/total customers
| 3.4681 | SAIDI=total G/total customers
| 11.521 | CAIDI=SAIDI/SAIFI
| 0.9996 | ASAI=total(customers*8760)-total G/total (customers*8760)
| 0.00039591 | ASUI=1-ASAI
| 12192.18 | ENS=total ENS*1000
| 11.0838 | AENS=ENS/total customers
CASE B
F1 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 1 | 220 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.545 | 12.9983 | 148.5 | 5247
| 2 | 220 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.545 | 12.9983 | 148.5 | 5247
| 3 | 220 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.545 | 12.9983 | 148.5 | 5247
| 4 | 220 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.545 | 12.9983 | 148.5 | 5247
| 5 | 200 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.5 | 11.925 | 135 | 4770
| 6 | 10 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.415 | 9.8978 | 6.75 | 238.5
| 7 | 10 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.415 | 9.8978 | 6.75 | 238.5
[11 empty] | 83.7135 | 742.5 | 26235
total customers | 1100
total (customers*8760) | 9636000
total F | 742.5
SAIFI=total F/total customers | 0.675
SAIDI=total G/total customers | 23.85
CAIDI=SAIDI/SAIFI | 35.3333
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99728
ASUI=1-ASAI | 0.0027226
ENS=total ENS*1000 | 83713.5
AENS=ENS/total customers | 76.1032
CASE C
F1 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 1 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 4.3975 | 14.9321 | 0.545 | 2.3966 | 64.79 | 967.45
| 2 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0 | 0 | 5 | 0
|  |  | 4 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 4.4463 | 14.6138 | 0.545 | 2.4232 | 66.935 | 978.175
| 3 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 4.3975 | 14.9321 | 0.545 | 2.3966 | 64.79 | 967.45
| 4 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.3075 |  | 4.4625 | 14.5122 | 0.545 | 2.4321 | 67.65 | 981.75
| 5 | 200 | 1 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 9 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 4.4463 | 14.6138 | 0.5 | 2.2231 | 60.85 | 889.25
| 6 | 10 | 1 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.3075 |  | 4.4625 | 14.5122 | 0.415 | 1.8519 | 3.075 | 44.625
| 7 | 10 | 1 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 12 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 4.4463 | 14.6138 | 0.415 | 1.8452 | 3.0425 | 44.4625
[11 empty] | 15.5688 | 331.1325 | 4873.1625
total customers | 1100
total (customers*8760) | 9636000
total F | 331.1325
SAIFI=total F/total customers | 0.30103
SAIDI=total G/total customers | 4.4301
CAIDI=SAIDI/SAIFI | 14.7167
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99949
ASUI=1-ASAI | 0.00050572
ENS=total ENS*1000 | 15568.8
AENS=ENS/total customers | 14.1535
CASE D
F1 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 1 | 220 | 1 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 6 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 8 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 9 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 3.816 | 5.6533 | 0.545 | 2.0797 | 148.5 | 839.52
| 2 | 220 | 1 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 8 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 9 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 3.856 | 5.7126 | 0.545 | 2.1015 | 148.5 | 848.32
| 3 | 220 | 1 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 4 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 9 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 3.816 | 5.6533 | 0.545 | 2.0797 | 148.5 | 839.52
| 4 | 220 | 1 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 4 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 6 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 7.049 | 10.443 | 0.545 | 3.8417 | 148.5 | 1550.78
| 5 | 200 | 1 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 4 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 6 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 7.049 | 10.443 | 0.5 | 3.5245 | 135 | 1409.8
| 6 | 10 | 1 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 4 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 6 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 8 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 9 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 7.049 | 10.443 | 0.415 | 2.9253 | 6.75 | 70.49
| 7 | 10 | 1 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 4 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 6 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 8 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 9 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 7.049 | 10.443 | 0.415 | 2.9253 | 6.75 | 70.49
[11 empty] | 19.4778 | 742.5 | 5628.92
total customers | 1100
total (customers*8760) | 9636000
total F | 742.5
SAIFI=total F/total customers | 0.675
SAIDI=total G/total customers | 5.1172
CAIDI=SAIDI/SAIFI | 7.581
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99942
ASUI=1-ASAI | 0.00058416
ENS=total ENS*1000 | 19477.835
AENS=ENS/total customers | 17.7071
CASE E
F1 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 1 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 0.5855 | 1.9881 | 0.545 | 0.3191 | 64.79 | 128.81
| 2 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 0.63425 | 2.0846 | 0.545 | 0.34567 | 66.935 | 139.535
| 3 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 0.5855 | 1.9881 | 0.545 | 0.3191 | 64.79 | 128.81
| 4 | 220 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.3075 |  | 0.6505 | 2.1154 | 0.545 | 0.35452 | 67.65 | 143.11
| 5 | 200 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 9 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 11 | 0.8 | 0 | 0 | 1 | 0
|  |  | 12 | 0.75 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 0.63425 | 2.0846 | 0.5 | 0.31713 | 60.85 | 126.85
| 6 | 10 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.3075 |  | 0.6505 | 2.1154 | 0.415 | 0.26996 | 3.075 | 6.505
| 7 | 10 | 1 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0 | 0 | 1 | 0
|  |  | 4 | 0.75 | 0 | 0 | 1 | 0
|  |  | 6 | 0.6 | 0 | 0 | 1 | 0
|  |  | 8 | 0.8 | 0 | 0 | 1 | 0
|  |  | 9 | 0.75 | 0 | 0 | 1 | 0
|  |  | 11 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 12 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.30425 |  | 0.63425 | 2.0846 | 0.415 | 0.26321 | 3.0425 | 6.3425
[11 empty] | 2.1887 | 331.1325 | 679.9625
total customers | 1100
total (customers*8760) | 9636000
total F | 331.1325
SAIFI=total F/total customers | 0.30103
SAIDI=total G/total customers | 0.61815
CAIDI=SAIDI/SAIFI | 2.0534
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99993
ASUI=1-ASAI | 7.0565e-05
ENS=total ENS*1000 | 2188.68
AENS=ENS/total customers | 1.9897
CASE F
F1 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 1 | 220 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 6 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 8 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 9 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 4.012 | 5.9437 | 0.545 | 2.1865 | 148.5 | 882.64
| 2 | 220 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 8 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 9 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 7.401 | 10.9644 | 0.545 | 4.0335 | 148.5 | 1628.22
| 3 | 220 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 9 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 10.75 | 15.9259 | 0.545 | 5.8588 | 148.5 | 2365
| 4 | 220 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 17.32 | 25.6593 | 0.545 | 9.4394 | 148.5 | 3810.4
| 5 | 200 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 12 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.675 |  | 17.32 | 25.6593 | 0.5 | 8.66 | 135 | 3464
| 6 | 10 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.415 | 9.8978 | 6.75 | 238.5
| 7 | 10 | 1 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 3 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 5 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 7 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 10 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 2 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 4 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 6 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 8 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 9 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 11 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 12 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.675 |  | 23.85 | 35.3333 | 0.415 | 9.8978 | 6.75 | 238.5
[11 empty] | 49.9737 | 742.5 | 12627.26
total customers | 1100
total (customers*8760) | 9636000
total F | 742.5
SAIFI=total F/total customers | 0.675
SAIDI=total G/total customers | 11.4793
CAIDI=SAIDI/SAIFI | 17.0064
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99869
ASUI=1-ASAI | 0.0013104
ENS=total ENS*1000 | 49973.735
AENS=ENS/total customers | 45.4307

## F2
CASE A & E
F2 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 8 | 1 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0 | 0 | 1 | 0
|  |  | 18 | 0.8 | 0 | 0 | 1 | 0
[6 empty] | 0.182 |  | 0.338 | 1.8571 | 1 | 0.338 | 0.182 | 0.338
| 9 | 1 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 14 | 0.6 | 0 | 0 | 1 | 0
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 18 | 0.8 | 0 | 0 | 1 | 0
[6 empty] | 0.19175 |  | 0.38675 | 2.0169 | 1.5 | 0.58013 | 0.19175 | 0.38675
| 10 | 1 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 14 | 0.6 | 0 | 0 | 1 | 0
|  |  | 16 | 0.75 | 0 | 0 | 1 | 0
|  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26
[6 empty] | 0.195 |  | 0.403 | 2.0667 | 1 | 0.403 | 0.195 | 0.403
[11 empty] | 1.3211 | 0.56875 | 1.1278
total customers | 3
total (customers*8760) | 26280
total F | 0.56875
SAIFI=total F/total customers | 0.18958
SAIDI=total G/total customers | 0.37592
CAIDI=SAIDI/SAIFI | 1.9829
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99996
ASUI=1-ASAI | 4.2913e-05
ENS=total ENS*1000 | 1321.125
AENS=ENS/total customers | 440.375
CASE B
F2 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 8 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 17 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26
[6 empty] | 0.28275 |  | 1.4138 | 5 | 1 | 1.4138 | 0.28275 | 1.4138
| 9 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 17 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26
[6 empty] | 0.28275 |  | 1.4138 | 5 | 1.5 | 2.1206 | 0.28275 | 1.4138
| 10 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 17 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26
[6 empty] | 0.28275 |  | 1.4138 | 5 | 1 | 1.4138 | 0.28275 | 1.4138
[11 empty] | 4.9481 | 0.84825 | 4.2412
total customers | 3
total (customers*8760) | 26280
total F | 0.84825
SAIFI=total F/total customers | 0.28275
SAIDI=total G/total customers | 1.4138
CAIDI=SAIDI/SAIFI | 5
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99984
ASUI=1-ASAI | 0.00016139
ENS=total ENS*1000 | 4948.125
AENS=ENS/total customers | 1649.375
CASE C
F1 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 8 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 17 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0 | 0 | 1 | 0
|  |  | 18 | 0.8 | 0 | 0 | 1 | 0
[6 empty] | 0.182 |  | 0.91 | 5 | 1 | 0.91 | 0.182 | 0.91
| 9 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 17 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 14 | 0.6 | 0 | 0 | 1 | 0
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 18 | 0.8 | 0 | 0 | 1 | 0
[6 empty] | 0.19175 |  | 0.95875 | 5 | 1.5 | 1.4381 | 0.19175 | 0.95875
| 10 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 17 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 14 | 0.6 | 0 | 0 | 1 | 0
|  |  | 16 | 0.75 | 0 | 0 | 1 | 0
|  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26
[6 empty] | 0.195 |  | 0.975 | 5 | 1 | 0.975 | 0.195 | 0.975
[11 empty] | 3.3231 | 0.56875 | 2.8438
total customers | 3
total (customers*8760) | 26280
total F | 0.56875
SAIFI=total F/total customers | 0.18958
SAIDI=total G/total customers | 0.94792
CAIDI=SAIDI/SAIFI | 5
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99989
ASUI=1-ASAI | 0.00010821
ENS=total ENS*1000 | 3323.125
AENS=ENS/total customers | 1107.7083
CASE D
F1 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 8 | 1 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 18 | 0.8 | 0.065 | 0.052 | 1 | 0.052
[6 empty] | 0.28275 |  | 0.43875 | 1.5517 | 1 | 0.43875 | 0.28275 | 0.43875
| 9 | 1 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 14 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 18 | 0.8 | 0.065 | 0.052 | 1 | 0.052
[6 empty] | 0.28275 |  | 0.47775 | 1.6897 | 1.5 | 0.71663 | 0.28275 | 0.47775
| 10 | 1 | 13 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 14 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26
[6 empty] | 0.28275 |  | 0.49075 | 1.7356 | 1 | 0.49075 | 0.28275 | 0.49075
[11 empty] | 1.6461 | 0.84825 | 1.4073
total customers | 3
total (customers*8760) | 26280
total F | 0.84825
SAIFI=total F/total customers | 0.28275
SAIDI=total G/total customers | 0.46908
CAIDI=SAIDI/SAIFI | 1.659
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99995
ASUI=1-ASAI | 5.3548e-05
ENS=total ENS*1000 | 1646.125
AENS=ENS/total customers | 548.7083
CASE F
F1 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 8 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 18 | 0.8 | 0.065 | 0.052 | 1 | 0.052
[6 empty] | 0.28275 |  | 0.64675 | 2.2874 | 1 | 0.64675 | 0.28275 | 0.64675
| 9 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 17 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 18 | 0.8 | 0.065 | 0.052 | 1 | 0.052
[6 empty] | 0.28275 |  | 1.0497 | 3.7126 | 1.5 | 1.5746 | 0.28275 | 1.0497
| 10 | 1 | 13 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 15 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 17 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 14 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 16 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 18 | 0.8 | 0.065 | 0.052 | 5 | 0.26
[6 empty] | 0.28275 |  | 1.4138 | 5 | 1 | 1.4138 | 0.28275 | 1.4138
[11 empty] | 3.6351 | 0.84825 | 3.1102
total customers | 3
total (customers*8760) | 26280
total F | 0.84825
SAIFI=total F/total customers | 0.28275
SAIDI=total G/total customers | 1.0367
CAIDI=SAIDI/SAIFI | 3.6667
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99988
ASUI=1-ASAI | 0.00011835
ENS=total ENS*1000 | 3635.125
AENS=ENS/total customers | 1211.7083

## F3
CASE A
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 11 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.29775 |  | 3.4908 | 11.7238 | 0.545 | 1.9025 | 65.505 | 767.965
| 12 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 3.4745 | 11.798 | 0.545 | 1.8936 | 64.79 | 764.39
| 13 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 3.4745 | 11.798 | 0.545 | 1.8936 | 64.79 | 764.39
| 14 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.28475 |  | 3.4257 | 12.0307 | 0.5 | 1.7129 | 56.95 | 685.15
| 15 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0.065 | 0 | 0 | 0
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 3.4745 | 11.798 | 0.5 | 1.7372 | 58.9 | 694.9
| 16 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0 | 0 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 3.4745 | 11.798 | 0.415 | 1.4419 | 2.945 | 34.745
| 17 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.28475 |  | 3.4257 | 12.0307 | 0.415 | 1.4217 | 2.8475 | 34.2575
[11 empty] | 12.0034 | 316.7275 | 3745.7975
total customers | 1080
total (customers*8760) | 9460800
total F | 316.7275
SAIFI=total F/total customers | 0.29327
SAIDI=total G/total customers | 3.4683
CAIDI=SAIDI/SAIFI | 11.8266
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.9996
ASUI=1-ASAI | 0.00039593
ENS=total ENS*1000 | 12003.3925
AENS=ENS/total customers | 11.1143
CASE B
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 11 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.66075 |  | 23.7787 | 35.9875 | 0.545 | 12.9594 | 145.365 | 5231.325
| 12 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.66075 |  | 23.7787 | 35.9875 | 0.545 | 12.9594 | 145.365 | 5231.325
| 13 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.66075 |  | 23.7787 | 35.9875 | 0.545 | 12.9594 | 145.365 | 5231.325
| 14 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.66075 |  | 23.7787 | 35.9875 | 0.5 | 11.8894 | 132.15 | 4755.75
| 15 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.66075 |  | 23.7787 | 35.9875 | 0.5 | 11.8894 | 132.15 | 4755.75
| 16 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.66075 |  | 23.7787 | 35.9875 | 0.415 | 9.8682 | 6.6075 | 237.7875
| 17 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.66075 |  | 23.7787 | 35.9875 | 0.415 | 9.8682 | 6.6075 | 237.7875
[11 empty] | 82.3934 | 713.61 | 25681.05
total customers | 1080
total (customers*8760) | 9460800
total F | 713.61
SAIFI=total F/total customers | 0.66075
SAIDI=total G/total customers | 23.7787
CAIDI=SAIDI/SAIFI | 35.9875
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99729
ASUI=1-ASAI | 0.0027145
ENS=total ENS*1000 | 82393.3688
AENS=ENS/total customers | 76.2902
CASE C
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 11 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0 | 0 | 5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.29775 |  | 4.4138 | 14.8237 | 0.545 | 2.4055 | 65.505 | 971.025
| 12 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0 | 0 | 5 | 0
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0 | 0 | 5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 4.3975 | 14.9321 | 0.545 | 2.3966 | 64.79 | 967.45
| 13 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0 | 0 | 5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 5 | 0
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0 | 0 | 5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 4.3975 | 14.9321 | 0.545 | 2.3966 | 64.79 | 967.45
| 14 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0 | 0 | 5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 5 | 0
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0 | 5 | 0
|  |  | 29 | 0.75 | 0 | 0 | 5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.28475 |  | 4.3487 | 15.2722 | 0.5 | 2.1744 | 56.95 | 869.75
| 15 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0 | 0 | 5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 5 | 0
|  |  | 25 | 0.6 | 0.065 | 0 | 5 | 0
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0 | 0 | 5 | 0
|  |  | 30 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 4.3975 | 14.9321 | 0.5 | 2.1987 | 58.9 | 879.5
| 16 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0 | 0 | 5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 5 | 0
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 4.3975 | 14.9321 | 0.415 | 1.825 | 2.945 | 43.975
| 17 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0 | 0 | 5 | 0
|  |  | 22 | 0.75 | 0 | 0 | 5 | 0
|  |  | 24 | 0.75 | 0 | 0 | 5 | 0
|  |  | 25 | 0.6 | 0 | 0 | 5 | 0
|  |  | 27 | 0.75 | 0 | 0 | 5 | 0
|  |  | 29 | 0.75 | 0.065 | 0 | 5 | 0
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.28475 |  | 4.3487 | 15.2722 | 0.415 | 1.8047 | 2.8475 | 43.4875
[11 empty] | 15.2016 | 316.7275 | 4742.6375
total customers | 1080
total (customers*8760) | 9460800
total F | 316.7275
SAIFI=total F/total customers | 0.29327
SAIDI=total G/total customers | 4.3913
CAIDI=SAIDI/SAIFI | 14.9739
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.9995
ASUI=1-ASAI | 0.00050129
ENS=total ENS*1000 | 15201.5875
AENS=ENS/total customers | 14.0755
CASE D
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 11 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 25 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.66075 |  | 3.8538 | 5.8324 | 0.545 | 2.1003 | 145.365 | 847.825
| 12 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 25 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.66075 |  | 3.8408 | 5.8127 | 0.545 | 2.0932 | 145.365 | 844.965
| 13 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.66075 |  | 6.9817 | 10.5664 | 0.545 | 3.8051 | 145.365 | 1535.985
| 14 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.66075 |  | 6.9817 | 10.5664 | 0.5 | 3.4909 | 132.15 | 1396.35
| 15 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 25 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.66075 |  | 3.8408 | 5.8127 | 0.5 | 1.9204 | 132.15 | 768.15
| 16 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 25 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.66075 |  | 6.9817 | 10.5664 | 0.415 | 2.8974 | 6.6075 | 69.8175
| 17 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 25 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.66075 |  | 6.9817 | 10.5664 | 0.415 | 2.8974 | 6.6075 | 69.8175
[11 empty] | 19.2047 | 713.61 | 5532.91
total customers | 1080
total (customers*8760) | 9460800
total F | 713.61
SAIFI=total F/total customers | 0.66075
SAIDI=total G/total customers | 5.1231
CAIDI=SAIDI/SAIFI | 7.7534
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99942
ASUI=1-ASAI | 0.00058482
ENS=total ENS*1000 | 19204.6587
AENS=ENS/total customers | 17.7821
CASE E
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 11 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.29775 |  | 0.64075 | 2.152 | 0.545 | 0.34921 | 65.505 | 140.965
| 12 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 0.6245 | 2.1205 | 0.545 | 0.34035 | 64.79 | 137.39
| 13 | 220 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 0.6245 | 2.1205 | 0.545 | 0.34035 | 64.79 | 137.39
| 14 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.28475 |  | 0.57575 | 2.0219 | 0.5 | 0.28787 | 56.95 | 115.15
| 15 | 200 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0.065 | 0 | 0 | 0
|  |  | 27 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 29 | 0.75 | 0 | 0 | 1 | 0
|  |  | 30 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 0.6245 | 2.1205 | 0.5 | 0.31225 | 58.9 | 124.9
| 16 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 30 | 0.6 | 0.065 | 0 | 0 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.2945 |  | 0.6245 | 2.1205 | 0.415 | 0.25917 | 2.945 | 6.245
| 17 | 10 | 19 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0 | 0 | 1 | 0
|  |  | 22 | 0.75 | 0 | 0 | 1 | 0
|  |  | 24 | 0.75 | 0 | 0 | 1 | 0
|  |  | 25 | 0.6 | 0 | 0 | 1 | 0
|  |  | 27 | 0.75 | 0 | 0 | 1 | 0
|  |  | 29 | 0.75 | 0.065 | 0 | 0 | 0
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.28475 |  | 0.57575 | 2.0219 | 0.415 | 0.23894 | 2.8475 | 5.7575
[11 empty] | 2.1281 | 316.7275 | 667.7975
total customers | 1080
total (customers*8760) | 9460800
total F | 316.7275
SAIFI=total F/total customers | 0.29327
SAIDI=total G/total customers | 0.61833
CAIDI=SAIDI/SAIFI | 2.1084
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99993
ASUI=1-ASAI | 7.0586e-05
ENS=total ENS*1000 | 2128.1425
AENS=ENS/total customers | 1.9705
CASE F
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 11 | 220 | 19 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 21 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 24 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 25 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 27 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 29 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.662 |  | 4.051 | 6.1193 | 0.545 | 2.2078 | 145.64 | 891.22
| 12 | 220 | 19 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 24 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 25 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 27 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 29 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.662 |  | 7.388 | 11.1601 | 0.545 | 4.0265 | 145.64 | 1625.36
| 13 | 220 | 19 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 24 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 29 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.662 |  | 13.918 | 21.0242 | 0.545 | 7.5853 | 145.64 | 3061.96
| 14 | 200 | 19 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 24 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 29 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.662 |  | 13.918 | 21.0242 | 0.5 | 6.959 | 132.4 | 2783.6
| 15 | 200 | 19 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 24 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 29 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 30 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.662 |  | 17.307 | 26.1435 | 0.5 | 8.6535 | 132.4 | 3461.4
| 16 | 10 | 19 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 24 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 29 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.662 |  | 23.785 | 35.929 | 0.415 | 9.8708 | 6.62 | 237.85
| 17 | 10 | 19 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 21 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 23 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 26 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 28 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 20 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 22 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 24 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 25 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 27 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 29 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 30 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.662 |  | 23.785 | 35.929 | 0.415 | 9.8708 | 6.62 | 237.85
[11 empty] | 49.1736 | 714.96 | 12299.24
total customers | 1080
total (customers*8760) | 9460800
total F | 714.96
SAIFI=total F/total customers | 0.662
SAIDI=total G/total customers | 11.3882
CAIDI=SAIDI/SAIFI | 17.2027
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.9987
ASUI=1-ASAI | 0.0013
ENS=total ENS*1000 | 49173.615
AENS=ENS/total customers | 45.5311

## F4
CASE A
F4 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 18 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 34 | 0.6 | 0 | 0 | 1 | 0
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 3.4908 | 11.2333 | 0.545 | 1.9025 | 68.365 | 767.965
| 19 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 1 | 0
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 3.442 | 11.4352 | 0.545 | 1.8759 | 66.22 | 757.24
| 20 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 1 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1 | 0
|  |  | 35 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 3.4908 | 11.2333 | 0.545 | 1.9025 | 68.365 | 767.965
| 21 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 1 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 3.4908 | 11.2333 | 0.545 | 1.9025 | 68.365 | 767.965
| 22 | 200 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 3.442 | 11.4352 | 0.5 | 1.721 | 60.2 | 688.4
| 23 | 200 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 3.4908 | 11.2333 | 0.5 | 1.7454 | 62.15 | 698.15
| 24 | 10 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 3.4908 | 11.2333 | 0.415 | 1.4487 | 3.1075 | 34.9075
| 25 | 10 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 3.442 | 11.4352 | 0.415 | 1.4284 | 3.01 | 34.42
[11 empty] | 13.9267 | 399.7825 | 4517.0125
total customers | 1300
total (customers*8760) | 11388000
total F | 399.7825
SAIFI=total F/total customers | 0.30753
SAIDI=total G/total customers | 3.4746
CAIDI=SAIDI/SAIFI | 11.2987
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.9996
ASUI=1-ASAI | 0.00039665
ENS=total ENS*1000 | 13926.7325
AENS=ENS/total customers | 10.7129
CASE B
F4 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 18 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.545 | 14.7395 | 160.38 | 5949.9
| 19 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.545 | 14.7395 | 160.38 | 5949.9
| 20 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.545 | 14.7395 | 160.38 | 5949.9
| 21 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.545 | 14.7395 | 160.38 | 5949.9
| 22 | 200 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.5 | 13.5225 | 145.8 | 5409
| 23 | 200 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.5 | 13.5225 | 145.8 | 5409
| 24 | 10 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.415 | 11.2237 | 7.29 | 270.45
| 25 | 10 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.415 | 11.2237 | 7.29 | 270.45
[11 empty] | 108.4505 | 947.7 | 35158.5
total customers | 1300
total (customers*8760) | 11388000
total F | 947.7
SAIFI=total F/total customers | 0.729
SAIDI=total G/total customers | 27.045
CAIDI=SAIDI/SAIFI | 37.0988
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99691
ASUI=1-ASAI | 0.0030873
ENS=total ENS*1000 | 108450.45
AENS=ENS/total customers | 83.4234
CASE C
F4 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 18 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 34 | 0.6 | 0 | 0 | 1 | 0
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 4.4787 | 14.4127 | 0.545 | 2.4409 | 68.365 | 985.325
| 19 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0 | 0 | 5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 4.43 | 14.7176 | 0.545 | 2.4144 | 66.22 | 974.6
| 20 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 5 | 0
|  |  | 35 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 37 | 0.75 | 0 | 0 | 5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 5 | 0
|  |  | 43 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 4.4787 | 14.4127 | 0.545 | 2.4409 | 68.365 | 985.325
| 21 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0 | 0 | 1 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 4.4787 | 14.4127 | 0.545 | 2.4409 | 68.365 | 985.325
| 22 | 200 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 5
|  |  | 35 | 0.75 | 0 | 0 | 5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 5 | 0
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0 | 0 | 5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 4.43 | 14.7176 | 0.5 | 2.215 | 60.2 | 886
| 23 | 200 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 4.4787 | 14.4127 | 0.5 | 2.2394 | 62.15 | 895.75
| 24 | 10 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 5
|  |  | 35 | 0.75 | 0 | 0 | 5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 5 | 0
|  |  | 42 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 4.4787 | 14.4127 | 0.415 | 1.8587 | 3.1075 | 44.7875
| 25 | 10 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 5
|  |  | 35 | 0.75 | 0 | 0 | 5 | 0
|  |  | 37 | 0.75 | 0 | 0 | 5 | 0
|  |  | 38 | 0.6 | 0 | 0 | 5 | 0
|  |  | 40 | 0.75 | 0 | 0 | 5 | 0
|  |  | 42 | 0.75 | 0 | 0 | 5 | 0
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 4.43 | 14.7176 | 0.415 | 1.8384 | 3.01 | 44.3
[11 empty] | 17.8886 | 399.7825 | 5801.4125
total customers | 1300
total (customers*8760) | 11388000
total F | 399.7825
SAIFI=total F/total customers | 0.30753
SAIDI=total G/total customers | 4.4626
CAIDI=SAIDI/SAIFI | 14.5114
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99949
ASUI=1-ASAI | 0.00050943
ENS=total ENS*1000 | 17888.6125
AENS=ENS/total customers | 13.7605
CASE D
F4 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 18 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 35 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 3.91 | 5.3635 | 0.545 | 2.131 | 160.38 | 860.2
| 19 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 7.051 | 9.6722 | 0.545 | 3.8428 | 160.38 | 1551.22
| 20 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 7.051 | 9.6722 | 0.545 | 3.8428 | 160.38 | 1551.22
| 21 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 34 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 35 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 7.051 | 9.6722 | 0.545 | 3.8428 | 160.38 | 1551.22
| 22 | 200 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 34 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 35 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 7.051 | 9.6722 | 0.5 | 3.5255 | 145.8 | 1410.2
| 23 | 200 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 34 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 35 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 3.91 | 5.3635 | 0.5 | 1.955 | 145.8 | 782
| 24 | 10 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 34 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 35 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 7.051 | 9.6722 | 0.415 | 2.9262 | 7.29 | 70.51
| 25 | 10 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 34 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 35 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 7.051 | 9.6722 | 0.415 | 2.9262 | 7.29 | 70.51
[11 empty] | 24.9922 | 947.7 | 7847.08
total customers | 1300
total (customers*8760) | 11388000
total F | 947.7
SAIFI=total F/total customers | 0.729
SAIDI=total G/total customers | 6.0362
CAIDI=SAIDI/SAIFI | 8.2801
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99931
ASUI=1-ASAI | 0.00068907
ENS=total ENS*1000 | 24992.165
AENS=ENS/total customers | 19.2247
CASE E
F4 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 18 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 34 | 0.6 | 0 | 0 | 1 | 0
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 0.64075 | 2.0619 | 0.545 | 0.34921 | 68.365 | 140.965
| 19 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 1 | 0
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 0.592 | 1.9668 | 0.545 | 0.32264 | 66.22 | 130.24
| 20 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 1 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1 | 0
|  |  | 35 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 0.64075 | 2.0619 | 0.545 | 0.34921 | 68.365 | 140.965
| 21 | 220 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 1 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 0.64075 | 2.0619 | 0.545 | 0.34921 | 68.365 | 140.965
| 22 | 200 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 0.592 | 1.9668 | 0.5 | 0.296 | 60.2 | 118.4
| 23 | 200 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 0.64075 | 2.0619 | 0.5 | 0.32038 | 62.15 | 128.15
| 24 | 10 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 43 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.31075 |  | 0.64075 | 2.0619 | 0.415 | 0.26591 | 3.1075 | 6.4075
| 25 | 10 | 31 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0 | 0 | 5 | 0
|  |  | 34 | 0.6 | 0 | 0 | 1
|  |  | 35 | 0.75 | 0 | 0 | 1 | 0
|  |  | 37 | 0.75 | 0 | 0 | 1 | 0
|  |  | 38 | 0.6 | 0 | 0 | 1 | 0
|  |  | 40 | 0.75 | 0 | 0 | 1 | 0
|  |  | 42 | 0.75 | 0 | 0 | 1 | 0
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 0.592 | 1.9668 | 0.415 | 0.24568 | 3.01 | 5.92
[11 empty] | 2.4982 | 399.7825 | 812.0125
total customers | 1300
total (customers*8760) | 11388000
total F | 399.7825
SAIFI=total F/total customers | 0.30753
SAIDI=total G/total customers | 0.62462
CAIDI=SAIDI/SAIFI | 2.0311
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99993
ASUI=1-ASAI | 7.1304e-05
ENS=total ENS*1000 | 2498.2325
AENS=ENS/total customers | 1.9217
CASE F
F4 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 18 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 35 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 4.118 | 5.6488 | 0.545 | 2.2443 | 160.38 | 905.96
| 19 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 10.648 | 14.6063 | 0.545 | 5.8032 | 160.38 | 2342.56
| 20 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 38 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 10.648 | 14.6063 | 0.545 | 5.8032 | 160.38 | 2342.56
| 21 | 220 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 17.178 | 23.5638 | 0.545 | 9.362 | 160.38 | 3779.16
| 22 | 200 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 17.178 | 23.5638 | 0.5 | 8.589 | 145.8 | 3435.6
| 23 | 200 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 43 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.729 |  | 20.567 | 28.2126 | 0.5 | 10.2835 | 145.8 | 4113.4
| 24 | 10 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.415 | 11.2237 | 7.29 | 270.45
| 25 | 10 | 31 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 33 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 36 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 39 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 41 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 32 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 34 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 35 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 37 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 38 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 40 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 42 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 43 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.729 |  | 27.045 | 37.0988 | 0.415 | 11.2237 | 7.29 | 270.45
[11 empty] | 64.5325 | 947.7 | 17460.14
total customers | 1300
total (customers*8760) | 11388000
total F | 947.7
SAIFI=total F/total customers | 0.729
SAIDI=total G/total customers | 13.4309
CAIDI=SAIDI/SAIFI | 18.4237
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99847
ASUI=1-ASAI | 0.0015332
ENS=total ENS*1000 | 64532.49
AENS=ENS/total customers | 49.6404

## F5
CASE A & E
F5 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 26 | 1 | 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0 | 0 | 1 | 0
|  |  | 49 | 0.6 | 0 | 0 | 1 | 0
[6 empty] | 0.1885 |  | 0.3835 | 2.0345 | 1 | 0.3835 | 0.1885 | 0.3835
| 27 | 1 | 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 45 | 0.75 | 0 | 0 | 1 | 0
|  |  | 47 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 49 | 0.6 | 0 | 0 | 1 | 0
[6 empty] | 0.19175 |  | 0.39975 | 2.0847 | 1 | 0.39975 | 0.19175 | 0.39975
| 28 | 1 | 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 45 | 0.75 | 0 | 0 | 1 | 0
|  |  | 47 | 0.8 | 0 | 0 | 1 | 0
|  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.17875 |  | 0.33475 | 1.8727 | 1 | 0.33475 | 0.17875 | 0.33475
[11 empty] | 1.118 | 0.559 | 1.118
total customers | 3
total (customers*8760) | 26280
total F | 0.559
SAIFI=total F/total customers | 0.18633
SAIDI=total G/total customers | 0.37267
CAIDI=SAIDI/SAIFI | 2
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99996
ASUI=1-ASAI | 4.2542e-05
ENS=total ENS*1000 | 1118
AENS=ENS/total customers | 372.6667
CASE B
F5 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 26 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 1.3975 | 5 | 1 | 1.3975 | 0.2795 | 1.3975
| 27 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 1.3975 | 5 | 1 | 1.3975 | 0.2795 | 1.3975
| 28 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 1.3975 | 5 | 1 | 1.3975 | 0.2795 | 1.3975
[11 empty] | 4.1925 | 0.8385 | 4.1925
total customers | 3
total (customers*8760) | 26280
total F | 0.8385
SAIFI=total F/total customers | 0.2795
SAIDI=total G/total customers | 1.3975
CAIDI=SAIDI/SAIFI | 5
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99984
ASUI=1-ASAI | 0.00015953
ENS=total ENS*1000 | 4192.5
AENS=ENS/total customers | 1397.5
CASE C
F5 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 26 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0 | 0 | 1 | 0
|  |  | 49 | 0.6 | 0 | 0 | 1 | 0
[6 empty] | 0.1885 |  | 0.9425 | 5 | 1 | 0.9425 | 0.1885 | 0.9425
| 27 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 45 | 0.75 | 0 | 0 | 1 | 0
|  |  | 47 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 49 | 0.6 | 0 | 0 | 1 | 0
[6 empty] | 0.19175 |  | 0.95875 | 5 | 1 | 0.95875 | 0.19175 | 0.95875
| 28 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 45 | 0.75 | 0 | 0 | 1 | 0
|  |  | 47 | 0.8 | 0 | 0 | 1 | 0
|  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.17875 |  | 0.89375 | 5 | 1 | 0.89375 | 0.17875 | 0.89375
[11 empty] | 2.795 | 0.559 | 2.795
total customers | 3
total (customers*8760) | 26280
total F | 0.559
SAIFI=total F/total customers | 0.18633
SAIDI=total G/total customers | 0.93167
CAIDI=SAIDI/SAIFI | 5
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99989
ASUI=1-ASAI | 0.00010635
ENS=total ENS*1000 | 2795
AENS=ENS/total customers | 931.6667
CASE D
F5 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 26 | 1 | 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 49 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[6 empty] | 0.2795 |  | 0.4745 | 1.6977 | 1 | 0.4745 | 0.2795 | 0.4745
| 27 | 1 | 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 47 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 49 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[6 empty] | 0.2795 |  | 0.4875 | 1.7442 | 1 | 0.4875 | 0.2795 | 0.4875
| 28 | 1 | 44 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 47 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 0.4355 | 1.5581 | 1 | 0.4355 | 0.2795 | 0.4355
[11 empty] | 1.3975 | 0.8385 | 1.3975
total customers | 3
total (customers*8760) | 26280
total F | 0.8385
SAIFI=total F/total customers | 0.2795
SAIDI=total G/total customers | 0.46583
CAIDI=SAIDI/SAIFI | 1.6667
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99995
ASUI=1-ASAI | 5.3177e-05
ENS=total ENS*1000 | 1397.5
AENS=ENS/total customers | 465.8333
CASE F
F5 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 26 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 49 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[6 empty] | 0.2795 |  | 0.6825 | 2.4419 | 1 | 0.6825 | 0.2795 | 0.6825
| 27 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 49 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[6 empty] | 0.2795 |  | 1.0465 | 3.7442 | 1 | 1.0465 | 0.2795 | 1.0465
| 28 | 1 | 44 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 46 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 48 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 45 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 47 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 49 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 1.3975 | 5 | 1 | 1.3975 | 0.2795 | 1.3975
[11 empty] | 3.1265 | 0.8385 | 3.1265
total customers | 3
total (customers*8760) | 26280
total F | 0.8385
SAIFI=total F/total customers | 0.2795
SAIDI=total G/total customers | 1.0422
CAIDI=SAIDI/SAIFI | 3.7287
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99988
ASUI=1-ASAI | 0.00011897
ENS=total ENS*1000 | 3126.5
AENS=ENS/total customers | 1042.1667

## F6
CASE A & E
F6 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 29 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 52 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0 | 0 | 1 | 0
|  |  | 55 | 0.6 | 0 | 0 | 1 | 0
[6 empty] | 0.19175 |  | 0.34775 | 1.8136 | 1 | 0.34775 | 0.19175 | 0.34775
| 30 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 52 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 51 | 0.6 | 0 | 0 | 1 | 0
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 55 | 0.6 | 0 | 0 | 1 | 0
[6 empty] | 0.2015 |  | 0.3965 | 1.9677 | 1 | 0.3965 | 0.2015 | 0.3965
| 31 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 52 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 51 | 0.6 | 0 | 0 | 1 | 0
|  |  | 53 | 0.75 | 0 | 0 | 1 | 0
|  |  | 55 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.19175 |  | 0.34775 | 1.8136 | 1.5 | 0.52163 | 0.19175 | 0.34775
[11 empty] | 1.2659 | 0.585 | 1.092
total customers | 3
total (customers*8760) | 26280
total F | 0.585
SAIFI=total F/total customers | 0.195
SAIDI=total G/total customers | 0.364
CAIDI=SAIDI/SAIFI | 1.8667
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99996
ASUI=1-ASAI | 4.1553e-05
ENS=total ENS*1000 | 1265.875
AENS=ENS/total customers | 421.9583
CASE B
F6 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 29 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 54 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 55 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 1.3975 | 5 | 1 | 1.3975 | 0.2795 | 1.3975
| 30 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 54 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 55 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 1.3975 | 5 | 1 | 1.3975 | 0.2795 | 1.3975
| 31 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 54 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 55 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 1.3975 | 5 | 1.5 | 2.0963 | 0.2795 | 1.3975
[11 empty] | 4.8913 | 0.8385 | 4.1925
total customers | 3
total (customers*8760) | 26280
total F | 0.8385
SAIFI=total F/total customers | 0.2795
SAIDI=total G/total customers | 1.3975
CAIDI=SAIDI/SAIFI | 5
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99984
ASUI=1-ASAI | 0.00015953
ENS=total ENS*1000 | 4891.25
AENS=ENS/total customers | 1630.4167
CASE C
F6 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 29 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 54 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0 | 0 | 1 | 0
|  |  | 55 | 0.6 | 0 | 0 | 1 | 0
[6 empty] | 0.19175 |  | 0.95875 | 5 | 1 | 0.95875 | 0.19175 | 0.95875
| 30 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 54 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 51 | 0.6 | 0 | 0 | 1 | 0
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 55 | 0.6 | 0 | 0 | 1 | 0
[6 empty] | 0.2015 |  | 1.0075 | 5 | 1 | 1.0075 | 0.2015 | 1.0075
| 31 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 54 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 51 | 0.6 | 0 | 0 | 1 | 0
|  |  | 53 | 0.75 | 0 | 0 | 1 | 0
|  |  | 55 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.19175 |  | 0.95875 | 5 | 1.5 | 1.4381 | 0.19175 | 0.95875
[11 empty] | 3.4044 | 0.585 | 2.925
total customers | 3
total (customers*8760) | 26280
total F | 0.585
SAIFI=total F/total customers | 0.195
SAIDI=total G/total customers | 0.975
CAIDI=SAIDI/SAIFI | 5
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99989
ASUI=1-ASAI | 0.0001113
ENS=total ENS*1000 | 3404.375
AENS=ENS/total customers | 1134.7917
CASE D
F6 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 29 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 52 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 55 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[6 empty] | 0.2795 |  | 0.4355 | 1.5581 | 1 | 0.4355 | 0.2795 | 0.4355
| 30 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 52 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 51 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 55 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[6 empty] | 0.2795 |  | 0.4745 | 1.6977 | 1 | 0.4745 | 0.2795 | 0.4745
| 31 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 52 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 51 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 55 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 0.4355 | 1.5581 | 1.5 | 0.65325 | 0.2795 | 0.4355
[11 empty] | 1.5633 | 0.8385 | 1.3455
total customers | 3
total (customers*8760) | 26280
total F | 0.8385
SAIFI=total F/total customers | 0.2795
SAIDI=total G/total customers | 0.4485
CAIDI=SAIDI/SAIFI | 1.6047
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99995
ASUI=1-ASAI | 5.1199e-05
ENS=total ENS*1000 | 1563.25
AENS=ENS/total customers | 521.0833
CASE F
F6 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 29 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 55 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[6 empty] | 0.2795 |  | 0.6305 | 2.2558 | 1 | 0.6305 | 0.2795 | 0.6305
| 30 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 54 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 55 | 0.6 | 0.065 | 0.039 | 1 | 0.039
[6 empty] | 0.2795 |  | 1.0335 | 3.6977 | 1 | 1.0335 | 0.2795 | 1.0335
| 31 | 1 | 50 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 52 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 54 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 51 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 53 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 55 | 0.6 | 0.065 | 0.039 | 5 | 0.195
[6 empty] | 0.2795 |  | 1.3975 | 5 | 1.5 | 2.0963 | 0.2795 | 1.3975
[11 empty] | 3.7603 | 0.8385 | 3.0615
total customers | 3
total (customers*8760) | 26280
total F | 0.8385
SAIFI=total F/total customers | 0.2795
SAIDI=total G/total customers | 1.0205
CAIDI=SAIDI/SAIFI | 3.6512
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99988
ASUI=1-ASAI | 0.0001165
ENS=total ENS*1000 | 3760.25
AENS=ENS/total customers | 1253.4167

## F7
CASE A
F7 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 32 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 3.494 | 11.608 | 0.545 | 1.9042 | 66.22 | 768.68
| 33 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 3.494 | 11.608 | 0.545 | 1.9042 | 66.22 | 768.68
| 34 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 3.429 | 11.9062 | 0.545 | 1.8688 | 63.36 | 754.38
| 35 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 3.494 | 11.608 | 0.545 | 1.9042 | 66.22 | 768.68
| 36 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 3.429 | 11.9062 | 0.5 | 1.7145 | 57.6 | 685.8
| 37 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0 | 0 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 3.494 | 11.608 | 0.5 | 1.747 | 60.2 | 698.8
| 38 | 10 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 3.429 | 11.9062 | 0.415 | 1.423 | 2.88 | 34.29
[11 empty] | 12.466 | 382.7 | 4479.31
total customers | 1290
total (customers*8760) | 11300400
total F | 382.7
SAIFI=total F/total customers | 0.29667
SAIDI=total G/total customers | 3.4723
CAIDI=SAIDI/SAIFI | 11.7045
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.9996
ASUI=1-ASAI | 0.00039639
ENS=total ENS*1000 | 12466.03
AENS=ENS/total customers | 9.6636
CASE B
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 32 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.664 |  | 23.795 | 35.8358 | 0.545 | 12.9683 | 146.08 | 5234.9
| 33 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.664 |  | 23.795 | 35.8358 | 0.545 | 12.9683 | 146.08 | 5234.9
| 34 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.664 |  | 23.795 | 35.8358 | 0.545 | 12.9683 | 146.08 | 5234.9
| 35 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.664 |  | 23.795 | 35.8358 | 0.545 | 12.9683 | 146.08 | 5234.9
| 36 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.664 |  | 23.795 | 35.8358 | 0.5 | 11.8975 | 132.8 | 4759
| 37 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.664 |  | 23.795 | 35.8358 | 0.5 | 11.8975 | 132.8 | 4759
| 38 | 10 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.664 |  | 23.795 | 35.8358 | 0.415 | 9.8749 | 6.64 | 237.95
[11 empty] | 85.543 | 856.56 | 30695.55
total customers | 1290
total (customers*8760) | 11300400
total F | 856.56
SAIFI=total F/total customers | 0.664
SAIDI=total G/total customers | 23.795
CAIDI=SAIDI/SAIFI | 35.8358
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99728
ASUI=1-ASAI | 0.0027163
ENS=total ENS*1000 | 85543.025
AENS=ENS/total customers | 66.3124
CASE C
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 32 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0 | 0 | 5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 4.43 | 14.7176 | 0.545 | 2.4144 | 66.22 | 974.6
| 33 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0 | 0 | 5 | 0
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0 | 0 | 5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 4.43 | 14.7176 | 0.545 | 2.4144 | 66.22 | 974.6
| 34 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0 | 0 | 5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 5 | 0
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0 | 0 | 5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 4.365 | 15.1562 | 0.545 | 2.3789 | 63.36 | 960.3
| 35 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0 | 0 | 5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 5 | 0
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0 | 5 | 0
|  |  | 66 | 0.8 | 0 | 0 | 5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 4.43 | 14.7176 | 0.545 | 2.4144 | 66.22 | 974.6
| 36 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0 | 0 | 5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 5 | 0
|  |  | 62 | 0.8 | 0.065 | 0 | 5 | 0
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0 | 0 | 5 | 0
|  |  | 67 | 0.6 | 0 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 4.365 | 15.1562 | 0.5 | 2.1825 | 57.6 | 873
| 37 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0 | 0 | 5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 5 | 0
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0 | 5 | 0
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 4.43 | 14.7176 | 0.5 | 2.215 | 60.2 | 886
| 38 | 10 | 56 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 5 | 0.24375
|  |  | 57 | 0.8 | 0 | 0 | 5 | 0
|  |  | 59 | 0.8 | 0 | 0 | 5 | 0
|  |  | 61 | 0.6 | 0 | 0 | 5 | 0
|  |  | 62 | 0.8 | 0 | 0 | 5 | 0
|  |  | 64 | 0.6 | 0 | 0 | 5 | 0
|  |  | 66 | 0.8 | 0.065 | 0 | 5 | 0
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 4.365 | 15.1562 | 0.415 | 1.8115 | 2.88 | 43.65
[11 empty] | 15.8309 | 382.7 | 5686.75
total customers | 1290
total (customers*8760) | 11300400
total F | 382.7
SAIFI=total F/total customers | 0.29667
SAIDI=total G/total customers | 4.4083
CAIDI=SAIDI/SAIFI | 14.8596
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.9995
ASUI=1-ASAI | 0.00050323
ENS=total ENS*1000 | 15830.95
AENS=ENS/total customers | 12.2721
CASE D
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 32 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 61 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 62 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.664 |  | 3.857 | 5.8087 | 0.545 | 2.1021 | 146.08 | 848.54
| 33 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 62 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.664 |  | 3.857 | 5.8087 | 0.545 | 2.1021 | 146.08 | 848.54
| 34 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 59 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.664 |  | 6.998 | 10.5392 | 0.545 | 3.8139 | 146.08 | 1539.56
| 35 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 59 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.664 |  | 6.998 | 10.5392 | 0.545 | 3.8139 | 146.08 | 1539.56
| 36 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 59 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 61 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 62 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.664 |  | 3.805 | 5.7304 | 0.5 | 1.9025 | 132.8 | 761
| 37 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 59 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 61 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 62 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.664 |  | 6.998 | 10.5392 | 0.5 | 3.499 | 132.8 | 1399.6
| 38 | 10 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 59 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 61 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 62 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.664 |  | 6.998 | 10.5392 | 0.415 | 2.9042 | 6.64 | 69.98
[11 empty] | 20.1376 | 856.56 | 7006.78
total customers | 1290
total (customers*8760) | 11300400
total F | 856.56
SAIFI=total F/total customers | 0.664
SAIDI=total G/total customers | 5.4316
CAIDI=SAIDI/SAIFI | 8.1801
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99938
ASUI=1-ASAI | 0.00062005
ENS=total ENS*1000 | 20137.62
AENS=ENS/total customers | 15.6106
CASE E
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 32 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 0.644 | 2.1395 | 0.545 | 0.35098 | 66.22 | 141.68
| 33 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 0.644 | 2.1395 | 0.545 | 0.35098 | 66.22 | 141.68
| 34 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 0.579 | 2.0104 | 0.545 | 0.31556 | 63.36 | 127.38
| 35 | 220 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0 | 0 | 0
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 0.644 | 2.1395 | 0.545 | 0.35098 | 66.22 | 141.68
| 36 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0 | 0 | 1 | 0
|  |  | 67 | 0.6 | 0 | 0 | 1 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 0.579 | 2.0104 | 0.5 | 0.2895 | 57.6 | 115.8
| 37 | 200 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0 | 0 | 0
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.301 |  | 0.644 | 2.1395 | 0.5 | 0.322 | 60.2 | 128.8
| 38 | 10 | 56 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 63 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 65 | 0.75 | 0.065 | 0.04875 | 1 | 0.04875
|  |  | 57 | 0.8 | 0 | 0 | 1 | 0
|  |  | 59 | 0.8 | 0 | 0 | 1 | 0
|  |  | 61 | 0.6 | 0 | 0 | 1 | 0
|  |  | 62 | 0.8 | 0 | 0 | 1 | 0
|  |  | 64 | 0.6 | 0 | 0 | 1 | 0
|  |  | 66 | 0.8 | 0.065 | 0 | 0 | 0
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 10 | 0.15
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
|  |  | x former |  |  | 0 | 0 | 0
[6 empty] | 0.288 |  | 0.579 | 2.0104 | 0.415 | 0.24029 | 2.88 | 5.79
[11 empty] | 2.2203 | 382.7 | 802.81
total customers | 1290
total (customers*8760) | 11300400
total F | 382.7
SAIFI=total F/total customers | 0.29667
SAIDI=total G/total customers | 0.62233
CAIDI=SAIDI/SAIFI | 2.0978
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99993
ASUI=1-ASAI | 7.1043e-05
ENS=total ENS*1000 | 2220.28
AENS=ENS/total customers | 1.7211
CASE F
F3 | Load point | customers | main | length | failure rate | length*failure rate | comp repair time | U=unavailability | overall repair | La | ENS=La*U | F=length*failure rate*customers | G=overall unavail *customers
| 32 | 220 | 56 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 58 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 60 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 63 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 65 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 61 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 62 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.665 |  | 4.054 | 6.0962 | 0.545 | 2.2094 | 146.3 | 891.88
| 33 | 220 | 56 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 63 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 65 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 62 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.665 |  | 7.403 | 11.1323 | 0.545 | 4.0346 | 146.3 | 1628.66
| 34 | 220 | 56 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 63 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 65 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.665 |  | 13.933 | 20.9519 | 0.545 | 7.5935 | 146.3 | 3065.26
| 35 | 220 | 56 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 63 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 65 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.665 |  | 13.933 | 20.9519 | 0.545 | 7.5935 | 146.3 | 3065.26
| 36 | 200 | 56 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 63 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 65 | 0.75 | 0.065 | 0.049 | 1 | 0.049
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 1 | 0.052
|  |  | 67 | 0.6 | 0.065 | 0.039 | 1 | 0.039
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 1 | 0.015
|  |  | x former |  |  | 0.015 | 1 | 0.015
[6 empty] | 0.665 |  | 17.27 | 25.9699 | 0.5 | 8.635 | 133 | 3454
| 37 | 200 | 56 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 63 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 65 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.665 |  | 23.8 | 35.7895 | 0.5 | 11.9 | 133 | 4760
| 38 | 10 | 56 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 58 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 60 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 63 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 65 | 0.75 | 0.065 | 0.049 | 5 | 0.245
|  |  | 57 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 59 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 61 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 62 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 64 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | 66 | 0.8 | 0.065 | 0.052 | 5 | 0.26
|  |  | 67 | 0.6 | 0.065 | 0.039 | 5 | 0.195
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
|  |  | x former |  |  | 0.015 | 200 | 3
[6 empty] | 0.665 |  | 23.8 | 35.7895 | 0.415 | 9.877 | 6.65 | 238
[11 empty] | 51.843 | 857.85 | 17103.06
total customers | 1290
total (customers*8760) | 11300400
total F | 857.85
SAIFI=total F/total customers | 0.665
SAIDI=total G/total customers | 13.2582
CAIDI=SAIDI/SAIFI | 19.9371
ASAI=total(customers*8760)-total G/total (customers*8760) | 0.99849
ASUI=1-ASAI | 0.0015135
ENS=total ENS*1000 | 51843.035
AENS=ENS/total customers | 40.1884

## Deviation
Case A | SAIFI |  | Case B | SAIFI |  | Case A | SAIDI |  | Case B | SAIDI |  | Case C | SAIDI |  | Case D | SAIDI |  | Case E | SAIDI | Case F | SAIDI
Feeder | Customers |  | F | Customers |  | F | Customers |  | F | Customers |  | F | Customers |  | F | Customers |  | F | Customers | F | Customers
331.1325 | 1100 |  | 742.5 | 1100 |  | 3814.9625 | 1100 |  | 26235 | 1100 |  | 4873.1625 | 1100 |  | 5628.92 | 1100 |  | 679.9625 | 1100 | 12627.26 | 1100
0.56875 | 3 |  | 0.84825 | 3 |  | 1.0465 | 3 |  | 4.2412 | 3 |  | 2.8438 | 3 |  | 1.4073 | 3 |  | 1.1278 | 3 | 3.1102 | 3
316.7275 | 1080 |  | 713.61 | 1080 |  | 3745.7975 | 1080 |  | 25681.05 | 1080 |  | 4742.6375 | 1080 |  | 5532.91 | 1080 |  | 667.7975 | 1080 | 12299.24 | 1080
399.7825 | 1300 |  | 947.7 | 1300 |  | 4517.0125 | 1300 |  | 35158.5 | 1300 |  | 5801.4125 | 1300 |  | 7847.08 | 1300 |  | 812.0125 | 1300 | 17460.14 | 1300
0.559 | 3 |  | 0.8385 | 3 |  | 1.118 | 3 |  | 4.1925 | 3 |  | 2.795 | 3 |  | 1.3975 | 3 |  | 1.118 | 3 | 3.1265 | 3
0.585 | 3 |  | 0.8385 | 3 |  | 1.092 | 3 |  | 4.1925 | 3 |  | 2.925 | 3 |  | 1.3455 | 3 |  | 1.092 | 3 | 3.0615 | 3
382.7 | 1290 |  | 856.56 | 1290 |  | 4479.31 | 1290 |  | 30695.55 | 1290 |  | 5686.75 | 1290 |  | 7006.78 | 1290 |  | 802.81 | 1290 | 17103.06 | 1290
1432.0553 | 4779 |  | 3262.8953 | 4779 |  | 16560.339 | 4779 |  | 117782.7263 | 4779 |  | 21112.5262 | 4779 |  | 26019.8402 | 4779 |  | 2965.9203 | 4779 | 59498.9983 | 4779
Sys | 0.29966 | Sys |  | 0.68276 |  | Sys | 3.4652 |  | Sys | 24.6459 |  | Sys | 4.4178 |  | Sys | 5.4446 |  | Sys | 0.62062 | Sys | 12.4501
| 0.2926 |  |  | 0.6704 |  |  | 3.5054 |  |  | 24.635 |  |  | 4.4524 |  |  | 5.4986 |  |  | 0.6252 |  | 12.4429
Deviation | 2.3546 |  | Deviation | 1.8099 |  | Deviation | -1.1592 |  | Deviation | 0.044201 |  | Deviation | -0.78386 |  | Deviation | -0.99143 |  | Deviation | -0.73874 | Deviation | 0.057781
CAIDI | [5 empty] | Sys | 11.564 |  | Sys | 36.0976 |  | Sys | 14.7428 |  | Sys | 7.9745 |  | Sys | 2.0711 | Sys | 18.235
[7 empty] | 11.8339 |  |  | 36.8438 |  |  | 15.0357 |  |  | 8.0769 |  |  | 2.0885 |  | 18.425
[6 empty] | Deviation | -2.3336 |  | Deviation | -2.0671 |  | Deviation | -1.9866 |  | Deviation | -1.2846 |  | Deviation | -0.84045 | Deviation | -1.0418
| Case A | ENS |  | Case B | ENS |  | Case C | ENS |  | Case D | ENS |  | Case E | ENS |  | Case F | ENS
| F | Customers |  | F | Customers |  | F | Customers |  | F | Customers |  | F | Customers |  | F | Customers
| 12192.18 | 1100 |  | 83713.5 | 1100 |  | 15568.8 | 1100 |  | 19477.835 | 1100 |  | 2188.68 | 1100 |  | 49973.735 | 1100
| 1321.125 | 3 |  | 4948.125 | 3 |  | 3323.125 | 3 |  | 1646.125 | 3 |  | 1321.125 | 3 |  | 3635.125 | 3
| 12003.3925 | 1080 |  | 82393.3688 | 1080 |  | 15201.5875 | 1080 |  | 19204.6587 | 1080 |  | 2128.1425 | 1080 |  | 49173.615 | 1080
| 13926.7325 | 1300 |  | 108450.45 | 1300 |  | 17888.6125 | 1300 |  | 24992.165 | 1300 |  | 2498.2325 | 1300 |  | 64532.49 | 1300
| 1118 | 3 |  | 4192.5 | 3 |  | 2795 | 3 |  | 1397.5 | 3 |  | 1118 | 3 |  | 3126.5 | 3
| 1265.875 | 3 |  | 4891.25 | 3 |  | 3404.375 | 3 |  | 1563.25 | 3 |  | 1265.875 | 3 |  | 3760.25 | 3
| 12466.03 | 1290 |  | 85543.025 | 1290 |  | 15830.95 | 1290 |  | 20137.62 | 1290 |  | 2220.28 | 1290 |  | 51843.035 | 1290
| 54293.335 | 4779 |  | 374132.2188 | 4779 |  | 74012.45 | 4779 |  | 88419.1537 | 4779 |  | 12740.335 | 4779 |  | 226044.75 | 4779
| Sys | 11.3608 |  | Sys | 78.2867 |  | Sys | 15.487 |  | Sys | 18.5016 |  | Sys | 2.6659 |  | Sys | 47.2996
AENS |  | 11.4619 |  |  | 79.053 |  |  | 15.6367 |  |  | 18.6932 |  |  | 2.7024 |  |  | 47.7777
| Deviation | -0.88977 |  | Deviation | -0.97882 |  | Deviation | -0.96651 |  | Deviation | -1.0356 |  | Deviation | -1.3692 |  | Deviation | -1.0108
ENS | Analytic | 54.2933 |  | Analytic | 374.1322 |  | Analytic | 74.0125 |  | Analytic | 88.4192 |  | Analytic | 12.7403 |  | Analytic | 226.0448
|  | 54.8272 |  |  | 373.9751 |  |  | 73.998 |  |  | 88.3791 |  |  | 12.7401 |  |  | 225.9202
| Deviation | -0.9833 |  | Deviation | 0.041996 |  | Deviation | 0.019524 |  | Deviation | 0.0453 |  | Deviation | 0.0018445 |  | Deviation | 0.0551